Water Operator Vault Practice Exam Packet

Questions are left-aligned. Choices are arranged in two columns and two rows. Answer keys begin on separate pages.

# Practice Exam 01 - Core Regulations, MCLs, and Operator Math

Batch ID: T5-20260619-E01-B1277

Question 1. The federal law that gives EPA authority to set national drinking water standards is:

| A) CERCLA | B) RCRA |
| --- | --- |
| C) Clean Water Act | D) Safe Drinking Water Act |

Question 2. A California T5 treatment operator is most associated with:

| A) wastewater collection | B) laboratory-only work |
| --- | --- |
| C) entry-level plant operation | D) advanced/chief-level treatment responsibility |

Question 3. Primary drinking water standards are mainly designed to protect:

| A) pipe color | B) taste and odor |
| --- | --- |
| C) billing accuracy | D) public health |

Question 4. Secondary drinking water standards are mainly related to:

| A) operator certification | B) health-based MCLs |
| --- | --- |
| C) aesthetics such as taste, odor, color, and staining | D) source capacity |

Question 5. The MCL for nitrate as nitrogen is:

| A) 10 mg/L | B) 1 mg/L |
| --- | --- |
| C) 45 mg/L | D) 5 mg/L |

Question 6. The MCL for nitrite as nitrogen is:

| A) 50 mg/L | B) 1 mg/L |
| --- | --- |
| C) 10 mg/L | D) 0.1 mg/L |

Question 7. The action level for lead under lead and copper rules is commonly expressed as:

| A) 0.050 mg/L | B) 0.005 mg/L |
| --- | --- |
| C) 0.015 mg/L | D) 0.010 mg/L |

Question 8. The action level for copper is commonly expressed as:

| A) 0.015 mg/L | B) 13 mg/L |
| --- | --- |
| C) 0.13 mg/L | D) 1.3 mg/L |

Question 9. The federal MCL for arsenic is:

| A) 0.050 mg/L | B) 0.010 mg/L |
| --- | --- |
| C) 0.005 mg/L | D) 1.0 mg/L |

Question 10. The MCL for TTHM is:

| A) 0.060 mg/L | B) 0.010 mg/L |
| --- | --- |
| C) 0.080 mg/L | D) 0.100 mg/L |

Question 11. The MCL for HAA5 is:

| A) 0.040 mg/L | B) 0.080 mg/L |
| --- | --- |
| C) 0.060 mg/L | D) 1.0 mg/L |

Question 12. A sample collected after water has remained motionless in premise plumbing is especially associated with:

| A) jar testing | B) well yield testing |
| --- | --- |
| C) turbidity profiling | D) lead and copper sampling |

Question 13. CT in disinfection means:

| A) chemical transfer | B) concentration times contact time |
| --- | --- |
| C) chlorine tested | D) corrosion trend |

Question 14. The basic chemical feed equation for pounds per day is:

| A) mg/L ÷ 8.34 | B) mg/L x MGD x 8.34 |
| --- | --- |
| C) gpm x psi | D) ft x ft x ft |

Question 15. A plant treats 4.0 MGD at 2.5 mg/L chlorine. Approximate chlorine feed is:

| A) 8.3 lb/day | B) 83.4 lb/day |
| --- | --- |
| C) 166.8 lb/day | D) 41.7 lb/day |

Question 16. A 2 MG basin has 1.5 MG usable volume. Flow is 3 MGD. The theoretical detention time is:

| A) 12 hr | B) 24 hr |
| --- | --- |
| C) 0.25 hr | D) 0.5 hr |

Question 17. A flow of 1 MGD is approximately:

| A) 8.34 gpm | B) 70 gpm |
| --- | --- |
| C) 694 gpm | D) 1,440 gpm |

Question 18. One cubic foot of water contains approximately:

| A) 3.14 gallons | B) 7.48 gallons |
| --- | --- |
| C) 1 gallon | D) 62.4 gallons |

Question 19. Water weighs approximately:

| A) 2.31 lb/gal | B) 62.4 lb/gal |
| --- | --- |
| C) 7.48 lb/gal | D) 8.34 lb/gal |

Question 20. A pressure of 1 psi equals approximately:

| A) 7.48 ft of head | B) 8.34 ft of head |
| --- | --- |
| C) 0.433 ft of head | D) 2.31 ft of head |

Question 21. The organism most resistant to normal chlorine disinfection is generally:

| A) Giardia | B) E. coli |
| --- | --- |
| C) total coliform | D) Cryptosporidium |

Question 22. Conventional filtration includes:

| A) fluoridation only | B) aeration only |
| --- | --- |
| C) coagulation, flocculation, sedimentation, filtration | D) softening only |

Question 23. Coagulation is primarily used to:

| A) raise nitrate | B) increase DBPs |
| --- | --- |
| C) add hardness | D) destabilize particles |

Question 24. Flocculation is primarily used to:

| A) gently mix particles into larger floc | B) destroy viruses |
| --- | --- |
| C) disinfect storage tanks | D) measure chlorine |

Question 25. Sedimentation removes particles mainly by:

| A) reverse osmosis | B) gravity settling |
| --- | --- |
| C) ion exchange | D) UV intensity |

Question 26. A high settled-water turbidity leaving sedimentation often increases loading on:

| A) distribution maps | B) billing software |
| --- | --- |
| C) fluoride tanks | D) filters |

Question 27. A sudden filter effluent turbidity spike can indicate:

| A) lower demand | B) filter breakthrough |
| --- | --- |
| C) lower particle loading | D) perfect coagulation |

Question 28. The main purpose of filter backwashing is to:

| A) raise alkalinity | B) reduce pump speed |
| --- | --- |
| C) add chlorine | D) remove accumulated solids and restore headloss |

Question 29. Disinfection byproducts generally increase when disinfectant reacts with:

| A) inert sand | B) sodium chloride only |
| --- | --- |
| C) nitrogen gas | D) natural organic matter |

Question 30. Chloramination is commonly used to:

| A) replace filtration | B) eliminate corrosion |
| --- | --- |
| C) remove all PFAS | D) maintain longer-lasting residual |

Question 31. Free chlorine residual is usually more reactive than:

| A) dissolved oxygen | B) chloramine residual |
| --- | --- |
| C) hardness | D) alkalinity |

Question 32. A cross-connection program is intended to prevent:

| A) backflow and contamination | B) overbilling |
| --- | --- |
| C) hydrant painting defects | D) pump cavitation only |

Question 33. Backpressure backflow can occur when downstream pressure is:

| A) higher than supply pressure | B) unrelated to pressure |
| --- | --- |
| C) lower than supply pressure | D) zero |

Question 34. Backsiphonage is commonly associated with:

| A) high hardness | B) excessive source nitrate |
| --- | --- |
| C) negative or reduced supply pressure | D) filter ripening |

Question 35. A boil water notice is most directly related to:

| A) pump efficiency | B) high electric use |
| --- | --- |
| C) low aesthetic color only | D) possible microbial risk |

Question 36. A loss of positive pressure in distribution is concerning because it can:

| A) reduce water age only | B) remove DBPs |
| --- | --- |
| C) allow intrusion | D) improve CT |

Question 37. The Revised Total Coliform Rule uses coliform detections to trigger:

| A) assessment and corrective action | B) filter-to-waste only |
| --- | --- |
| C) meter replacement | D) fluoride feed |

Question 38. E. coli detection in a routine bacteriological sample is generally more serious than total coliform alone because it indicates:

| A) fecal contamination potential | B) high hardness |
| --- | --- |
| C) low alkalinity | D) scaling |

Question 39. The best first action after a confirmed critical analyzer alarm is to:

| A) increase all feeds blindly | B) ignore it until shift change |
| --- | --- |
| C) disable SCADA alarms | D) verify the reading and assess process impact |

Question 40. Jar testing is used to evaluate:

| A) meter reading | B) staffing level |
| --- | --- |
| C) coagulation dose and treatment response | D) well casing depth |

Question 41. Alkalinity is important in coagulation because it affects:

| A) pH buffering and chemical reactions | B) motor voltage only |
| --- | --- |
| C) sample bottle color | D) pipe diameter only |

Question 42. Low pH can increase risk of:

| A) nitrate formation | B) pipe enlargement |
| --- | --- |
| C) turbidity disappearance | D) corrosion |

Question 43. High pH can reduce effectiveness of:

| A) free chlorine disinfection | B) pipe labels |
| --- | --- |
| C) SCADA screenshots | D) meter routes |

Question 44. PFAS treatment options commonly include:

| A) GAC, ion exchange, RO | B) aeration only |
| --- | --- |
| C) fluoridation | D) sedimentation only |

Question 45. Granular activated carbon removes contaminants mainly by:

| A) bacteriological growth | B) adsorption |
| --- | --- |
| C) pH neutralization only | D) gravity alone |

Question 46. Ion exchange removes target ions by:

| A) adding sand | B) exchanging ions on a resin |
| --- | --- |
| C) raising temperature | D) ultraviolet light |

Question 47. Reverse osmosis removes many dissolved contaminants by:

| A) pressure-driven membrane separation | B) open-channel settling |
| --- | --- |
| C) chlorine demand | D) aeration turbulence |

Question 48. A pump losing prime is most directly a problem with:

| A) fluoride MCL | B) high finished water chlorine |
| --- | --- |
| C) suction/air leakage or insufficient liquid | D) jar-test color |

Question 49. Cavitation is associated with:

| A) normal lubrication only | B) vapor bubbles forming/collapsing in pump zones |
| --- | --- |
| C) high fluoride | D) stable suction conditions |

Question 50. A good operator log entry should be:

| A) vague | B) clear, timely, factual, and traceable |
| --- | --- |
| C) written days later | D) opinion-only |

# Answer Key - Practice Exam 01 - Core Regulations, MCLs, and Operator Math

Batch ID: T5-20260619-E01-B1277

| Q | Answer | Review |
| --- | --- | --- |
| 1 | D | source-supported with caveats |
| 2 | D | source-supported with caveats |
| 3 | D | source-supported with caveats |
| 4 | C | source-supported with caveats |
| 5 | A | source-supported with caveats |
| 6 | B | source-supported with caveats |
| 7 | C | source-supported with caveats |
| 8 | D | source-supported with caveats |
| 9 | B | source-supported with caveats |
| 10 | C | source-supported with caveats |
| 11 | C | source-supported with caveats |
| 12 | D | source-supported with caveats |
| 13 | B | source-supported with caveats |
| 14 | B | source-supported with caveats |
| 15 | B | source-supported with caveats |
| 16 | A | source-supported with caveats |
| 17 | C | source-supported with caveats |
| 18 | B | source-supported with caveats |
| 19 | D | source-supported with caveats |
| 20 | D | source-supported with caveats |
| 21 | D | source-supported with caveats |
| 22 | C | source-supported with caveats |
| 23 | D | source-supported with caveats |
| 24 | A | source-supported with caveats |
| 25 | B | source-supported with caveats |
| 26 | D | source-supported with caveats |
| 27 | B | source-supported with caveats |
| 28 | D | source-supported with caveats |
| 29 | D | source-supported with caveats |
| 30 | D | source-supported with caveats |
| 31 | B | source-supported with caveats |
| 32 | A | source-supported with caveats |
| 33 | A | source-supported with caveats |
| 34 | C | source-supported with caveats |
| 35 | D | source-supported with caveats |
| 36 | C | source-supported with caveats |
| 37 | A | source-supported with caveats |
| 38 | A | source-supported with caveats |
| 39 | D | source-supported with caveats |
| 40 | C | source-supported with caveats |
| 41 | A | source-supported with caveats |
| 42 | D | source-supported with caveats |
| 43 | A | source-supported with caveats |
| 44 | A | source-supported with caveats |
| 45 | B | source-supported with caveats |
| 46 | B | source-supported with caveats |
| 47 | A | source-supported with caveats |
| 48 | C | source-supported with caveats |
| 49 | B | source-supported with caveats |
| 50 | B | source-supported with caveats |

# Practice Exam 02 - Treatment Processes and Water Quality

Batch ID: T5-20260619-E02-B3057

Question 1. The purpose of rapid mix is to:

| A) flush hydrants | B) disinfect tanks |
| --- | --- |
| C) disperse coagulant quickly | D) settle sludge |

Question 2. Overmixing during flocculation may:

| A) shear floc apart | B) lower pipe pressure |
| --- | --- |
| C) remove arsenic automatically | D) increase clearwell volume |

Question 3. Poor coagulation can lead to:

| A) lower particle count always | B) short filter runs and higher turbidity |
| --- | --- |
| C) lower chlorine demand always | D) no effect on filters |

Question 4. Alum addition can consume alkalinity and may:

| A) lower pH | B) eliminate DBPs |
| --- | --- |
| C) increase pH always | D) remove all PFAS |

Question 5. Ferric coagulants may be useful for:

| A) pump lubrication | B) particle and some organic removal |
| --- | --- |
| C) meter sizing | D) billing accuracy |

Question 6. Polymer feed is often used to:

| A) aid floc formation | B) remove backflow hazards |
| --- | --- |
| C) raise nitrate | D) replace all disinfectants |

Question 7. A jar test result should be evaluated by:

| A) taste only | B) color of the clipboard |
| --- | --- |
| C) turbidity, floc formation, settling, and process goals | D) pump brand |

Question 8. Filter ripening means:

| A) filter media turning biological only | B) reservoir turnover |
| --- | --- |
| C) pipe corrosion | D) initial period after backwash before optimal performance |

Question 9. Filter breakthrough means:

| A) particles pass through filter as removal worsens | B) chlorine increases automatically |
| --- | --- |
| C) headloss disappears | D) filter becomes new |

Question 10. Filter-to-waste is used to:

| A) bypass sampling | B) increase plant output |
| --- | --- |
| C) keep poor initial filter effluent out of finished water | D) reduce reporting |

Question 11. Headloss through a filter generally increases as:

| A) solids accumulate | B) demand decreases only |
| --- | --- |
| C) water becomes warmer only | D) SCADA logs clear |

Question 12. A turbidity meter should be:

| A) ignored if online | B) calibrated/verified according to procedures |
| --- | --- |
| C) cleaned once per year only | D) replaced after each sample |

Question 13. Turbidity is important because particles can:

| A) prove water is sterile | B) shield pathogens and indicate treatment performance |
| --- | --- |
| C) lower all DBPs | D) remove lead |

Question 14. Direct filtration differs from conventional filtration because it generally lacks:

| A) sedimentation | B) coagulation |
| --- | --- |
| C) monitoring | D) disinfection |

Question 15. Slow sand filtration relies heavily on:

| A) biological layer and fine media | B) high-rate chemical feed only |
| --- | --- |
| C) pressure membranes | D) ion exchange resin |

Question 16. Membrane integrity testing is used to detect:

| A) chlorine decay | B) pump cavitation |
| --- | --- |
| C) defects that could allow particle/pathogen passage | D) billing errors |

Question 17. RO concentrate management matters because concentrate may contain:

| A) only sand | B) no dissolved solids |
| --- | --- |
| C) pure oxygen only | D) elevated rejected contaminants |

Question 18. GAC beds require monitoring for:

| A) pump RPM only | B) pipe paint |
| --- | --- |
| C) breakthrough/exhaustion | D) meter routes |

Question 19. An ion exchange nitrate system requires attention to:

| A) turbidity spikes only | B) brine handling and regeneration |
| --- | --- |
| C) UV dose only | D) backflow colors |

Question 20. Aeration is commonly used for:

| A) CT replacement | B) lead sampling |
| --- | --- |
| C) RO concentrate only | D) volatile compounds, gases, taste/odor, or oxidation support |

Question 21. Packed tower aeration increases contact between:

| A) coagulant and sludge | B) resin and brine |
| --- | --- |
| C) fluoride and lime | D) air and water |

Question 22. Taste and odor compounds are often addressed with:

| A) PAC/GAC, oxidation, source control | B) meter replacement |
| --- | --- |
| C) higher billing rates | D) pressure gauges only |

Question 23. Ozone is a strong oxidant but can form:

| A) nitrate always | B) copper pipe |
| --- | --- |
| C) lead scale | D) bromate when bromide is present |

Question 24. UV disinfection effectiveness depends on:

| A) only tank color | B) hardness only |
| --- | --- |
| C) fluoride feed | D) UV dose, transmittance, lamp condition, and flow |

Question 25. Chlorine dioxide can create:

| A) pump headloss | B) lead action levels |
| --- | --- |
| C) sand carryover only | D) chlorite/chlorate concerns |

Question 26. Free ammonia with chlorine can contribute to:

| A) nitrification risk in chloraminated systems | B) lower bacteria always |
| --- | --- |
| C) less monitoring | D) lower water age |

Question 27. Nitrification in distribution can cause:

| A) stable residual only | B) loss of chloramine residual and nitrite/nitrate issues |
| --- | --- |
| C) lower HPC always | D) no pH change ever |

Question 28. Water age is important because it can affect:

| A) pipe diameter immediately | B) certified operator grade |
| --- | --- |
| C) residual decay and DBP formation | D) elevation datum |

Question 29. Finished-water pH is important for:

| A) flow unit labels | B) employee schedules |
| --- | --- |
| C) corrosion control and disinfectant performance | D) hydrant color |

Question 30. Alkalinity acts as:

| A) bacterial indicator | B) pH buffering capacity |
| --- | --- |
| C) taste panel | D) pump speed |

Question 31. Hardness is mainly associated with:

| A) lead and copper only | B) calcium and magnesium |
| --- | --- |
| C) ozone and bromide | D) chlorine and ammonia |

Question 32. Softening may be used to reduce:

| A) hardness | B) color from logs only |
| --- | --- |
| C) viruses only | D) DBPs only |

Question 33. Lime softening can raise:

| A) PFAS | B) chlorine demand always |
| --- | --- |
| C) nitrate | D) pH |

Question 34. Corrosion control commonly uses:

| A) less monitoring | B) pH/alkalinity adjustment or corrosion inhibitors |
| --- | --- |
| C) larger sample bottles only | D) more turbidity |

Question 35. Orthophosphate is often used to:

| A) disinfect wells | B) regenerate resin |
| --- | --- |
| C) form protective corrosion-control films | D) backwash filters |

Question 36. A sudden increase in chlorine demand may indicate:

| A) lower risk | B) clean analyzers only |
| --- | --- |
| C) organic loading, ammonia, contamination, or process change | D) lower source water reactivity |

Question 37. Color in raw water can be caused by:

| A) fluoridation only | B) natural organic matter, metals, or algae |
| --- | --- |
| C) pipe maps | D) pressure gauges |

Question 38. Algae can affect treatment by:

| A) lowering coagulant need always | B) eliminating DBPs |
| --- | --- |
| C) improving all filters | D) causing taste/odor, filter clogging, toxins, and pH swings |

Question 39. Cyanotoxin response should include:

| A) only increasing pump speed | B) source monitoring, treatment evaluation, and regulatory coordination |
| --- | --- |
| C) ignoring blooms | D) stopping records |

Question 40. Turbidity standards for filtered water are linked to:

| A) employee hours | B) pathogen removal performance |
| --- | --- |
| C) customer class | D) service meter age |

Question 41. A clearwell provides:

| A) accounting | B) raw water screening |
| --- | --- |
| C) storage and contact time | D) coagulant only |

Question 42. Baffling improves CT by:

| A) lowering disinfectant strength always | B) increasing raw turbidity |
| --- | --- |
| C) removing PFAS | D) reducing short-circuiting |

Question 43. T10 is used in CT calculations to estimate:

| A) pump horsepower | B) effective contact time |
| --- | --- |
| C) sludge age | D) tank height only |

Question 44. Higher flow through a contact basin usually:

| A) has no effect | B) increases detention time |
| --- | --- |
| C) eliminates need for residual | D) reduces detention/contact time |

Question 45. A low clearwell level may reduce:

| A) plant voltage | B) finished hardness |
| --- | --- |
| C) raw water algae | D) available contact time and storage reserve |

Question 46. The best response to failing CT is to:

| A) disable analyzer | B) ignore if water looks clear |
| --- | --- |
| C) evaluate flow, residual, pH, temperature, and contact time; correct before delivery | D) write it down later only |

Question 47. Turbidity, chlorine residual, pH, and temperature matter for:

| A) hydrant color | B) billing |
| --- | --- |
| C) disinfection compliance evaluation | D) staffing schedule only |

Question 48. A chemical day tank should have:

| A) no secondary containment ever | B) no labels |
| --- | --- |
| C) open top only | D) labeling, containment, and safe handling controls |

Question 49. Sodium hypochlorite degrades faster with:

| A) darkness and cool storage | B) lower age only |
| --- | --- |
| C) heat, sunlight, age, and high concentration | D) no air exposure only |

Question 50. Chemical compatibility is important because mixing incompatible chemicals can:

| A) lower risk | B) improve all treatment |
| --- | --- |
| C) eliminate PPE | D) create dangerous reactions or gas release |

# Answer Key - Practice Exam 02 - Treatment Processes and Water Quality

Batch ID: T5-20260619-E02-B3057

| Q | Answer | Review |
| --- | --- | --- |
| 1 | C | source-supported with caveats |
| 2 | A | source-supported with caveats |
| 3 | B | source-supported with caveats |
| 4 | A | source-supported with caveats |
| 5 | B | source-supported with caveats |
| 6 | A | source-supported with caveats |
| 7 | C | source-supported with caveats |
| 8 | D | source-supported with caveats |
| 9 | A | source-supported with caveats |
| 10 | C | source-supported with caveats |
| 11 | A | source-supported with caveats |
| 12 | B | source-supported with caveats |
| 13 | B | source-supported with caveats |
| 14 | A | source-supported with caveats |
| 15 | A | source-supported with caveats |
| 16 | C | source-supported with caveats |
| 17 | D | source-supported with caveats |
| 18 | C | source-supported with caveats |
| 19 | B | source-supported with caveats |
| 20 | D | source-supported with caveats |
| 21 | D | source-supported with caveats |
| 22 | A | source-supported with caveats |
| 23 | D | source-supported with caveats |
| 24 | D | source-supported with caveats |
| 25 | D | source-supported with caveats |
| 26 | A | source-supported with caveats |
| 27 | B | source-supported with caveats |
| 28 | C | source-supported with caveats |
| 29 | C | source-supported with caveats |
| 30 | B | source-supported with caveats |
| 31 | B | source-supported with caveats |
| 32 | A | source-supported with caveats |
| 33 | D | source-supported with caveats |
| 34 | B | source-supported with caveats |
| 35 | C | source-supported with caveats |
| 36 | C | source-supported with caveats |
| 37 | B | source-supported with caveats |
| 38 | D | source-supported with caveats |
| 39 | B | source-supported with caveats |
| 40 | B | source-supported with caveats |
| 41 | C | source-supported with caveats |
| 42 | D | source-supported with caveats |
| 43 | B | source-supported with caveats |
| 44 | D | source-supported with caveats |
| 45 | D | source-supported with caveats |
| 46 | C | source-supported with caveats |
| 47 | C | source-supported with caveats |
| 48 | D | source-supported with caveats |
| 49 | C | source-supported with caveats |
| 50 | D | source-supported with caveats |

# Practice Exam 03 - Source Water, Distribution, Sampling, and Public Health

Batch ID: T5-20260619-E03-B6080

Question 1. Groundwater under direct influence of surface water is important because it may require:

| A) only billing changes | B) no disinfection |
| --- | --- |
| C) no monitoring | D) surface-water-type treatment evaluation |

Question 2. A sanitary survey evaluates:

| A) operator pay | B) customer water bills only |
| --- | --- |
| C) system facilities, sources, operations, and potential contamination risks | D) vehicle mileage |

Question 3. Wellhead protection focuses on:

| A) increasing DBPs | B) preventing contamination near wells |
| --- | --- |
| C) lowering records | D) raising hardness |

Question 4. A damaged well seal can allow:

| A) surface contamination into a well | B) more CT |
| --- | --- |
| C) lower turbidity always | D) lower nitrate always |

Question 5. Nitrate in groundwater is often associated with:

| A) UV lamps | B) fertilizer, septic, animal waste, or agricultural influence |
| --- | --- |
| C) pipe paint | D) meter reading |

Question 6. Arsenic in groundwater can be:

| A) only from chlorine | B) naturally occurring/geologic |
| --- | --- |
| C) only from customer plumbing | D) only from cross-connections |

Question 7. Iron and manganese often cause:

| A) acute microbial disease | B) immediate CT failure |
| --- | --- |
| C) staining, color, and taste complaints | D) lower pH always |

Question 8. A watershed protection program helps reduce:

| A) sample bottle cost | B) source contamination and treatment burden |
| --- | --- |
| C) billing errors | D) pump horsepower only |

Question 9. Reservoir turnover can cause:

| A) no water quality impact ever | B) lower water age always |
| --- | --- |
| C) lower DBPs always | D) water quality changes, taste/odor, turbidity, or manganese release |

Question 10. A source water algae bloom may increase:

| A) taste/odor and treatment challenge | B) service meter age |
| --- | --- |
| C) operator certification grade | D) pump efficiency |

Question 11. A distribution system should maintain positive pressure to:

| A) remove PFAS | B) reduce intrusion risk |
| --- | --- |
| C) lower source capacity | D) increase water age |

Question 12. Dead ends can contribute to:

| A) lower DBPs always | B) higher residual always |
| --- | --- |
| C) high water age and residual loss | D) no operational concerns |

Question 13. Flushing programs help manage:

| A) lead action levels directly | B) employee training only |
| --- | --- |
| C) sediment, water age, taste/odor, and residual | D) source nitrate only |

Question 14. Storage tanks should be inspected for:

| A) meter reads | B) office supplies |
| --- | --- |
| C) sanitary integrity, vents, hatches, screens, coatings, and sediment | D) payroll |

Question 15. A missing vent screen on a finished water tank is a concern because it can allow:

| A) lower hardness | B) lower chlorine demand |
| --- | --- |
| C) insects/animals/debris entry | D) more CT |

Question 16. Tank stratification can affect:

| A) residual, temperature, and water quality | B) sample custody only |
| --- | --- |
| C) pipe labels only | D) billing only |

Question 17. Backflow assemblies are installed to:

| A) improve taste only | B) protect the public water system from hazards |
| --- | --- |
| C) replace disinfection | D) increase source yield |

Question 18. An air gap is generally considered:

| A) a chemical feed pump | B) a sample preservative |
| --- | --- |
| C) a type of chlorine residual | D) a reliable physical separation |

Question 19. Reduced pressure principle assemblies are commonly used for:

| A) well pumping | B) higher-hazard cross-connection protection |
| --- | --- |
| C) filter ripening | D) only aesthetic complaints |

Question 20. A bacteriological sample tap should be:

| A) selected randomly without a plan only | B) clean, representative, and free from attachments that contaminate samples |
| --- | --- |
| C) from a garden hose | D) leaking |

Question 21. Chain of custody is used to:

| A) calculate pump horsepower | B) adjust coagulant dose |
| --- | --- |
| C) document sample handling from collection to analysis | D) assign operator grade |

Question 22. Holding times are important because:

| A) results improve with age | B) labels fade only |
| --- | --- |
| C) sample quality can change before analysis | D) bottles get heavier |

Question 23. A field chlorine residual should usually be measured:

| A) at or near collection time | B) only when positive |
| --- | --- |
| C) after mailing sample | D) one week later |

Question 24. A total coliform positive sample may indicate:

| A) good disinfectant only | B) possible pathway for contamination |
| --- | --- |
| C) hardness only | D) fluoride overdose |

Question 25. E. coli positive repeat sample requires serious attention because it can indicate:

| A) fecal contamination risk | B) low manganese |
| --- | --- |
| C) high color only | D) normal aesthetics |

Question 26. A Level 1 or Level 2 assessment under coliform rules is meant to:

| A) replace all pipes | B) find and correct sanitary defects |
| --- | --- |
| C) reduce pressure intentionally | D) cancel monitoring |

Question 27. Public notification tiers are based on:

| A) customer income | B) seriousness and urgency of the violation/situation |
| --- | --- |
| C) pump age | D) pipe material only |

Question 28. Tier 1 public notice is generally for:

| A) annual aesthetic notes only | B) immediate health-risk situations |
| --- | --- |
| C) meter testing | D) routine reports only |

Question 29. Consumer Confidence Reports communicate:

| A) annual water quality information to customers | B) chemical invoices |
| --- | --- |
| C) hydrant painting schedules | D) operator timesheets |

Question 30. A treatment technique is:

| A) a customer class | B) an optional taste test |
| --- | --- |
| C) a required process/control when direct MCL measurement may not be practical | D) a pump brand |

Question 31. Turbidity performance requirements in filtration are an example of:

| A) treatment performance control | B) fluoridation permit |
| --- | --- |
| C) service line inventory only | D) billing category |

Question 32. Acute contaminants are those that can:

| A) only stain fixtures | B) pose health risks from short-term exposure |
| --- | --- |
| C) only affect taste | D) never require notice |

Question 33. Nitrate is often treated as an acute concern because it can affect:

| A) pipe paint | B) meter registers |
| --- | --- |
| C) infants by methemoglobinemia risk | D) pump motors |

Question 34. Legionella risk is influenced by:

| A) fluoride feed only | B) raw water altitude only |
| --- | --- |
| C) warm water, stagnation, and poor building water management | D) filter sand only |

Question 35. Giardia is commonly controlled by:

| A) billing | B) meter replacement |
| --- | --- |
| C) filtration and disinfection/inactivation | D) corrosion coupons only |

Question 36. Cryptosporidium is challenging because it is:

| A) removed by copper only | B) resistant to normal chlorination |
| --- | --- |
| C) created by lime | D) measured by pH alone |

Question 37. A vulnerability assessment helps identify:

| A) security and operational weaknesses | B) annual leave balances |
| --- | --- |
| C) pipe thread type | D) coagulant color |

Question 38. Emergency response planning should include:

| A) roles, communications, backup resources, and priority actions | B) only old phone lists |
| --- | --- |
| C) no mutual aid | D) no exercises |

Question 39. A main break can create water quality risk because it may cause:

| A) lower bacteria always | B) depressurization and intrusion |
| --- | --- |
| C) perfect flushing | D) lower water age always |

Question 40. After distribution repairs, operators commonly perform:

| A) no verification | B) flushing, disinfection, pressure restoration, and sampling as required |
| --- | --- |
| C) filter backwash only | D) billing only |

Question 41. Low distribution residual at a distant site could indicate:

| A) perfect mixing | B) too much CT only |
| --- | --- |
| C) low risk | D) high water age, demand, nitrification, or contamination |

Question 42. A customer taste/odor complaint cluster should trigger:

| A) automatic blame of plumbing only | B) no log entry |
| --- | --- |
| C) pattern review, field checks, and treatment/distribution investigation | D) no samples |

Question 43. A pressure zone is controlled by:

| A) operator grade | B) elevation, pumps, tanks, and valves |
| --- | --- |
| C) lab bottle type | D) fluoride feed |

Question 44. PRVs are used to:

| A) disinfect tanks | B) increase hardness |
| --- | --- |
| C) reduce/control downstream pressure | D) remove arsenic |

Question 45. Air relief valves help:

| A) release trapped air from pipelines | B) increase chlorine dose |
| --- | --- |
| C) remove PFAS | D) sample lead |

Question 46. A hydrant flushing plan should consider:

| A) no sample points | B) no traffic control ever |
| --- | --- |
| C) direction, velocity, residual, turbidity, and customer impacts | D) only paint color |

Question 47. A storage tank overflow event should be assessed for:

| A) only water waste billing | B) sanitary risk, intrusion potential, and operational cause |
| --- | --- |
| C) no consequence | D) pump efficiency only |

Question 48. Finished water storage should be protected from:

| A) sunlight only | B) customer notices |
| --- | --- |
| C) contamination, animals, unauthorized access, and cross-connections | D) higher elevation |

Question 49. A representative sample is one that:

| A) is unpreserved regardless of method | B) reflects the water quality being evaluated |
| --- | --- |
| C) is always first water from any tap | D) is taken from the easiest hose |

Question 50. The most defensible compliance record is:

| A) accurate, complete, timely, and retained according to requirements | B) kept only verbally |
| --- | --- |
| C) reconstructed from memory | D) overwritten monthly |

# Answer Key - Practice Exam 03 - Source Water, Distribution, Sampling, and Public Health

Batch ID: T5-20260619-E03-B6080

| Q | Answer | Review |
| --- | --- | --- |
| 1 | D | source-supported with caveats |
| 2 | C | source-supported with caveats |
| 3 | B | source-supported with caveats |
| 4 | A | source-supported with caveats |
| 5 | B | source-supported with caveats |
| 6 | B | source-supported with caveats |
| 7 | C | source-supported with caveats |
| 8 | B | source-supported with caveats |
| 9 | D | source-supported with caveats |
| 10 | A | source-supported with caveats |
| 11 | B | source-supported with caveats |
| 12 | C | source-supported with caveats |
| 13 | C | source-supported with caveats |
| 14 | C | source-supported with caveats |
| 15 | C | source-supported with caveats |
| 16 | A | source-supported with caveats |
| 17 | B | source-supported with caveats |
| 18 | D | source-supported with caveats |
| 19 | B | source-supported with caveats |
| 20 | B | source-supported with caveats |
| 21 | C | source-supported with caveats |
| 22 | C | source-supported with caveats |
| 23 | A | source-supported with caveats |
| 24 | B | source-supported with caveats |
| 25 | A | source-supported with caveats |
| 26 | B | source-supported with caveats |
| 27 | B | source-supported with caveats |
| 28 | B | source-supported with caveats |
| 29 | A | source-supported with caveats |
| 30 | C | source-supported with caveats |
| 31 | A | source-supported with caveats |
| 32 | B | source-supported with caveats |
| 33 | C | source-supported with caveats |
| 34 | C | source-supported with caveats |
| 35 | C | source-supported with caveats |
| 36 | B | source-supported with caveats |
| 37 | A | source-supported with caveats |
| 38 | A | source-supported with caveats |
| 39 | B | source-supported with caveats |
| 40 | B | source-supported with caveats |
| 41 | D | source-supported with caveats |
| 42 | C | source-supported with caveats |
| 43 | B | source-supported with caveats |
| 44 | C | source-supported with caveats |
| 45 | A | source-supported with caveats |
| 46 | C | source-supported with caveats |
| 47 | B | source-supported with caveats |
| 48 | C | source-supported with caveats |
| 49 | B | source-supported with caveats |
| 50 | A | source-supported with caveats |

# Practice Exam 04 - Advanced Math, Pumps, SCADA, and Operations

Batch ID: T5-20260619-E04-B1890

Question 1. The formula for flow in a channel using area and velocity is:

| A) Q = psi x ft | B) Q = C x T |
| --- | --- |
| C) Q = A x V | D) Q = mg/L x 8.34 |

Question 2. A pipe flowing full has area 3 ft² and velocity 4 ft/s. Flow is:

| A) 7 ft³/s | B) 16 ft³/s |
| --- | --- |
| C) 24 ft³/s | D) 12 ft³/s |

Question 3. One ft³/s is approximately:

| A) 694 gpm | B) 448.8 gpm |
| --- | --- |
| C) 62.4 gpm | D) 7.48 gpm |

Question 4. 12 ft³/s is approximately:

| A) 694 gpm | B) 448 gpm |
| --- | --- |
| C) 5386 gpm | D) 1200 gpm |

Question 5. A basin volume of 500,000 gal at 2 MGD gives detention time of:

| A) 12 hr | B) 0.25 hr |
| --- | --- |
| C) 6 hr | D) 24 hr |

Question 6. A 90-minute detention time equals:

| A) 1.5 hr | B) 90 hr |
| --- | --- |
| C) 0.9 hr | D) 9 hr |

Question 7. Chlorine residual is 1.8 mg/L and effective contact time is 40 min. CT is:

| A) 180 | B) 72 |
| --- | --- |
| C) 4.5 | D) 40 |

Question 8. If required CT is 60 and actual CT is 72, the condition is:

| A) impossible | B) unrelated |
| --- | --- |
| C) passing with margin | D) failing |

Question 9. If flow doubles through the same contact volume, theoretical detention time:

| A) halves | B) stays the same |
| --- | --- |
| C) doubles | D) becomes zero |

Question 10. A chemical dose of 12 mg/L at 6 MGD equals:

| A) 60 lb/day | B) 300 lb/day |
| --- | --- |
| C) 1200 lb/day | D) 600 lb/day |

Question 11. A 12.5% hypochlorite solution is roughly:

| A) no active chlorine | B) pure chlorine gas |
| --- | --- |
| C) 0.125 lb available chlorine per lb solution | D) 12.5 lb per gallon exactly always |

Question 12. Feed pump calibration checks:

| A) actual output versus expected setting | B) tank color |
| --- | --- |
| C) office temperature | D) pipe age |

Question 13. A drawdown test measures:

| A) chemical feed pump output | B) filter breakthrough |
| --- | --- |
| C) billing demand | D) well casing corrosion only |

Question 14. Pump head is commonly expressed in:

| A) feet | B) MCL |
| --- | --- |
| C) NTU | D) mg/L |

Question 15. Total dynamic head includes:

| A) static lift, pressure head, friction losses, and minor losses | B) only pipe color |
| --- | --- |
| C) only tank diameter | D) chlorine residual |

Question 16. Pump efficiency compares:

| A) water horsepower output to brake horsepower input | B) CT to T10 |
| --- | --- |
| C) pH to alkalinity | D) MCL to AL |

Question 17. Cavitation can be caused by:

| A) low DBPs only | B) excess fluoride only |
| --- | --- |
| C) inadequate NPSH | D) high source alkalinity only |

Question 18. A pump curve shows relationship between:

| A) flow and head | B) turbidity and MCL |
| --- | --- |
| C) pH and chlorine | D) lead and copper |

Question 19. Operating too far from best efficiency point can cause:

| A) vibration, heat, wear, or poor performance | B) no concern |
| --- | --- |
| C) lower energy always | D) perfect operation always |

Question 20. A check valve helps prevent:

| A) nitrification | B) turbidity calibration |
| --- | --- |
| C) coagulation | D) reverse flow |

Question 21. A pressure gauge reading 100 psi is approximately:

| A) 100 ft head | B) 231 ft head |
| --- | --- |
| C) 748 ft head | D) 43 ft head |

Question 22. A tank water surface elevation 120 ft above a service point gives about:

| A) 277 psi | B) 52 psi |
| --- | --- |
| C) 120 psi | D) 231 psi |

Question 23. SCADA trend review is useful because it can show:

| A) no historical value | B) replacement for operators |
| --- | --- |
| C) only current weather | D) process changes over time |

Question 24. An alarm setpoint should be:

| A) disabled during busy shifts | B) random |
| --- | --- |
| C) unknown | D) meaningful, documented, and tied to response actions |

Question 25. Instrument calibration records should document:

| A) next vacation | B) date, standard, result, adjustment, and person |
| --- | --- |
| C) opinions only | D) nothing if passed |

Question 26. A failed chlorine analyzer should be handled by:

| A) ignoring residual | B) verification, repair/calibration, and backup monitoring |
| --- | --- |
| C) no sample collection | D) disabling disinfection |

Question 27. Redundancy in critical systems means:

| A) no spare parts | B) backup equipment or alternate path exists |
| --- | --- |
| C) fewer safeguards | D) single point failure only |

Question 28. Lockout/tagout is used to:

| A) control hazardous energy during maintenance | B) improve taste |
| --- | --- |
| C) increase chlorine | D) sample lead |

Question 29. Confined space entry requires:

| A) no monitoring | B) no attendant ever |
| --- | --- |
| C) hazard evaluation and controls before entry | D) only a flashlight |

Question 30. Chemical PPE is selected based on:

| A) weather only | B) chemical hazard and SDS |
| --- | --- |
| C) operator preference only | D) pipe diameter |

Question 31. SDS information helps identify:

| A) hazards, handling, storage, PPE, and response | B) jar test dose only |
| --- | --- |
| C) consumer confidence rules | D) pump curves |

Question 32. Secondary containment is used to:

| A) contain spills/leaks | B) lower CT |
| --- | --- |
| C) raise residual | D) flush mains |

Question 33. A chlorine gas leak response should emphasize:

| A) ignoring odor | B) untrained entry |
| --- | --- |
| C) life safety, alarms, evacuation/isolation, and trained response | D) opening all doors blindly |

Question 34. Hypochlorite and acid contact can release:

| A) chlorine gas | B) harmless sand |
| --- | --- |
| C) nitrate | D) oxygen only |

Question 35. Hypochlorite and ammonia mixing can form:

| A) manganese | B) lead scale only |
| --- | --- |
| C) chloramines and potentially hazardous vapors | D) arsenic |

Question 36. Preventive maintenance is intended to:

| A) replace records | B) increase emergency repairs |
| --- | --- |
| C) avoid inspections | D) reduce failure likelihood and extend equipment life |

Question 37. A critical spare-parts list should focus on:

| A) parts that would limit safe production if unavailable | B) random bolts only |
| --- | --- |
| C) decorative items | D) expired chemicals |

Question 38. Root cause analysis asks:

| A) what color alarm was | B) how to hide it |
| --- | --- |
| C) why the failure happened and how recurrence can be prevented | D) who to blame only |

Question 39. A near-miss report is valuable because it:

| A) eliminates PPE | B) identifies hazards before injury or failure occurs |
| --- | --- |
| C) replaces training | D) proves nothing happened |

Question 40. The best response to an unexplained finished-water quality shift is to:

| A) guess blindly | B) wait a week |
| --- | --- |
| C) turn off logs | D) verify data, check instruments, review process, and escalate as needed |

Question 41. Standard operating procedures should be:

| A) never revised | B) current, accessible, and used consistently |
| --- | --- |
| C) verbal only | D) secret |

Question 42. A valve closed in the wrong position can cause:

| A) perfect mixing | B) no impact ever |
| --- | --- |
| C) lower all risk | D) pressure, flow, or water quality problems |

Question 43. A pressure surge/water hammer can damage:

| A) only pH | B) pipes, valves, meters, and pumps |
| --- | --- |
| C) only paperwork | D) only alkalinity |

Question 44. Soft starts or VFDs help manage:

| A) jar testing only | B) lead sampling |
| --- | --- |
| C) nitrate removal only | D) motor starting and speed control |

Question 45. A VFD changes pump speed by controlling:

| A) sample time | B) chlorine concentration |
| --- | --- |
| C) motor frequency | D) tank coating |

Question 46. Electrical work should be performed by:

| A) anyone during shift | B) only if dry floor exists |
| --- | --- |
| C) untrained staff | D) qualified personnel following safety procedures |

Question 47. Backup power planning should consider:

| A) customer bills | B) no exercise testing |
| --- | --- |
| C) critical loads, fuel, testing, and transfer equipment | D) only office lights |

Question 48. A mutual-aid agreement helps provide:

| A) lower chemical dose | B) automatic MCL waiver |
| --- | --- |
| C) emergency support resources | D) routine payroll |

Question 49. A plant shutdown decision should prioritize:

| A) public health, compliance, and safe operating limits | B) hiding alarms |
| --- | --- |
| C) avoiding paperwork | D) convenience only |

Question 50. The most useful shift handoff includes:

| A) current status, abnormal conditions, work in progress, and needed actions | B) jokes only |
| --- | --- |
| C) no details | D) old weather |

# Answer Key - Practice Exam 04 - Advanced Math, Pumps, SCADA, and Operations

Batch ID: T5-20260619-E04-B1890

| Q | Answer | Review |
| --- | --- | --- |
| 1 | C | source-supported with caveats |
| 2 | D | source-supported with caveats |
| 3 | B | source-supported with caveats |
| 4 | C | source-supported with caveats |
| 5 | C | source-supported with caveats |
| 6 | A | source-supported with caveats |
| 7 | B | source-supported with caveats |
| 8 | C | source-supported with caveats |
| 9 | A | source-supported with caveats |
| 10 | D | source-supported with caveats |
| 11 | C | source-supported with caveats |
| 12 | A | source-supported with caveats |
| 13 | A | source-supported with caveats |
| 14 | A | source-supported with caveats |
| 15 | A | source-supported with caveats |
| 16 | A | source-supported with caveats |
| 17 | C | source-supported with caveats |
| 18 | A | source-supported with caveats |
| 19 | A | source-supported with caveats |
| 20 | D | source-supported with caveats |
| 21 | B | source-supported with caveats |
| 22 | B | source-supported with caveats |
| 23 | D | source-supported with caveats |
| 24 | D | source-supported with caveats |
| 25 | B | source-supported with caveats |
| 26 | B | source-supported with caveats |
| 27 | B | source-supported with caveats |
| 28 | A | source-supported with caveats |
| 29 | C | source-supported with caveats |
| 30 | B | source-supported with caveats |
| 31 | A | source-supported with caveats |
| 32 | A | source-supported with caveats |
| 33 | C | source-supported with caveats |
| 34 | A | source-supported with caveats |
| 35 | C | source-supported with caveats |
| 36 | D | source-supported with caveats |
| 37 | A | source-supported with caveats |
| 38 | C | source-supported with caveats |
| 39 | B | source-supported with caveats |
| 40 | D | source-supported with caveats |
| 41 | B | source-supported with caveats |
| 42 | D | source-supported with caveats |
| 43 | B | source-supported with caveats |
| 44 | D | source-supported with caveats |
| 45 | C | source-supported with caveats |
| 46 | D | source-supported with caveats |
| 47 | C | source-supported with caveats |
| 48 | C | source-supported with caveats |
| 49 | A | source-supported with caveats |
| 50 | A | source-supported with caveats |

# Practice Exam 05 - Scenario Judgment, Compliance, and Troubleshooting

Batch ID: T5-20260619-E05-B5325

Question 1. Raw water turbidity rises rapidly after a storm. The operator should first:

| A) increase awareness, verify process response, and adjust treatment based on data | B) ignore it |
| --- | --- |
| C) disable turbidity alarms | D) stop all records |

Question 2. Finished water turbidity exceeds an internal alarm limit. The best first response is:

| A) delete trend | B) lower coagulant blindly |
| --- | --- |
| C) assume sensor failure only | D) verify reading and protect finished water quality |

Question 3. A filter has repeated short runs. Likely review should include:

| A) coagulation, flocculation, loading, backwash, and media condition | B) office lighting |
| --- | --- |
| C) operator seniority | D) customer bills |

Question 4. A jar test shows best turbidity at a higher coagulant dose but lower pH. Next concern is:

| A) alkalinity/pH control and downstream impacts | B) sample label color |
| --- | --- |
| C) pump paint | D) vehicle fuel |

Question 5. A filter turbidity spike occurs immediately after backwash. A useful control is:

| A) filter-to-waste or ripening procedure | B) bypassing all monitoring |
| --- | --- |
| C) raising pH blindly | D) no action |

Question 6. CT is marginal during peak flow. Operator options include:

| A) ignore peak flow | B) lower residual |
| --- | --- |
| C) remove contact basin | D) reduce flow, increase residual if allowed, increase storage/contact, or adjust operations |

Question 7. Clearwell level drops unexpectedly. First priority is:

| A) shut off alarms | B) wait until morning |
| --- | --- |
| C) paperwork only | D) confirm cause and assess CT/storage/supply impacts |

Question 8. Chlorine residual leaving the plant suddenly drops. The operator should check:

| A) hydrant paint | B) only office email |
| --- | --- |
| C) analyzer, feed system, chemical strength, demand, flow, and sampling | D) meter reading |

Question 9. A hypochlorite feed pump loses prime. The immediate concern is:

| A) loss of disinfectant feed | B) high hardness only |
| --- | --- |
| C) high nitrate | D) DBP overcompliance |

Question 10. A chemical feed line ruptures. First priority is:

| A) finish paperwork first | B) wash to storm drain |
| --- | --- |
| C) safety, containment, isolation, notification, and treatment continuity | D) ignore if small |

Question 11. A customer reports oily water. Best response is:

| A) tell them it is normal always | B) no record |
| --- | --- |
| C) treat as a potential contamination complaint and investigate promptly | D) only flush next year |

Question 12. A single taste complaint may be less significant than:

| A) a normal pH | B) a clustered pattern across an area or pressure zone |
| --- | --- |
| C) an old map | D) a routine log |

Question 13. A main break in a low-pressure area requires attention to:

| A) no bacteriological concern | B) only asphalt repair |
| --- | --- |
| C) intrusion risk, isolation, repair disinfection, flushing, and sampling | D) changing operator grade |

Question 14. After a power failure, operators should verify:

| A) treatment continuity, alarms, pumps, residuals, pressure, and backup systems | B) nothing if power returns |
| --- | --- |
| C) only building lights | D) only clock time |

Question 15. SCADA communication fails but plant continues running. Best action is:

| A) switch to local/manual monitoring procedures and restore communications | B) stop all samples |
| --- | --- |
| C) leave site | D) assume all values are perfect |

Question 16. A chlorine analyzer reads zero but grab sample shows 1.2 mg/L. Likely next step:

| A) troubleshoot/calibrate analyzer while relying on verified grab checks | B) increase chlorine wildly |
| --- | --- |
| C) ignore both | D) report no chlorine immediately without verification |

Question 17. If online pH differs greatly from bench pH, the operator should:

| A) verify calibration, sample location, and analyzer condition | B) ignore bench data |
| --- | --- |
| C) disable pH control | D) average them blindly |

Question 18. A plant receives a chemical delivery. Before unloading, verify:

| A) chemical identity, delivery paperwork, tank, connections, and safety controls | B) tank color only |
| --- | --- |
| C) weather only | D) driver music |

Question 19. Offloading the wrong chemical can cause:

| A) improved treatment always | B) severe safety and treatment consequences |
| --- | --- |
| C) no issue if diluted | D) lower risk |

Question 20. A coagulant overdose may cause:

| A) no impacts | B) perfect water always |
| --- | --- |
| C) poor water quality, pH depression, residual metals, or filter issues | D) zero sludge |

Question 21. A coagulant underdose may cause:

| A) poor floc and higher turbidity | B) automatic disinfection |
| --- | --- |
| C) lower turbidity always | D) no filter impact |

Question 22. A filter backwash valve fails closed. The likely concern is:

| A) high fluoride | B) inability to clean filter properly |
| --- | --- |
| C) extra CT | D) lower water age |

Question 23. A filter backwash waste valve fails open. The likely concern is:

| A) better production | B) no concern |
| --- | --- |
| C) water loss and possible process/control issue | D) higher storage |

Question 24. A raw water pump vibration alarm should prompt:

| A) lower chlorine | B) more coagulant |
| --- | --- |
| C) ignore until failure | D) inspection, trend review, and possible shutdown before damage |

Question 25. Bearing overheating may indicate:

| A) lubrication, alignment, load, or mechanical problems | B) low nitrate |
| --- | --- |
| C) good pump condition always | D) high CT |

Question 26. A sudden pressure drop in distribution may indicate:

| A) main break, pump/tank issue, valve change, or demand surge | B) stable operation always |
| --- | --- |
| C) better residual | D) lower risk |

Question 27. A closed valve after maintenance should be documented because:

| A) documents are decorative | B) no one needs to know |
| --- | --- |
| C) valve position affects hydraulics and response | D) it prevents all breaks |

Question 28. Unauthorized access at a tank site should trigger:

| A) lowering chlorine | B) security response and sanitary assessment |
| --- | --- |
| C) only repainting | D) no action |

Question 29. A bird or animal found inside a finished-water tank requires:

| A) immediate sanitary response, isolation/evaluation, disinfection/sampling, and notification as needed | B) billing entry |
| --- | --- |
| C) routine note only | D) no concern if small |

Question 30. A positive E. coli result should not be treated as:

| A) routine aesthetic complaint | B) investigation trigger |
| --- | --- |
| C) regulatory matter | D) potential acute health concern |

Question 31. A monitoring violation means:

| A) required sample/reporting was missed or invalid | B) pump failed |
| --- | --- |
| C) bill is late | D) water is always unsafe |

Question 32. A treatment technique violation means:

| A) customer called | B) operator forgot lunch |
| --- | --- |
| C) required treatment/process control was not met | D) sample bottle broke only |

Question 33. An MCL violation means:

| A) lower turbidity | B) only aesthetics |
| --- | --- |
| C) missing SDS | D) contaminant limit was exceeded according to compliance rules |

Question 34. An action level exceedance for lead/copper is different from an MCL because it:

| A) triggers required actions rather than functioning as a standard MCL | B) is only a lab typo |
| --- | --- |
| C) requires no response | D) applies to raw water only |

Question 35. A Tier 1 notice requires rapid communication because:

| A) it is only aesthetic | B) immediate health risk may exist |
| --- | --- |
| C) it is optional | D) it is annual only |

Question 36. Operational data should be reviewed before making major dose changes because:

| A) only lab data matters yearly | B) dose changes never matter |
| --- | --- |
| C) trends are useless | D) trends help prevent overcorrection |

Question 37. Multiple small abnormal signs together should be treated as:

| A) less important than one sign | B) random only |
| --- | --- |
| C) reason to stop logs | D) possible developing failure pattern |

Question 38. A good troubleshooting sequence is:

| A) blame, ignore, repeat | B) guess, adjust, leave |
| --- | --- |
| C) verify, isolate, diagnose, correct, document, monitor | D) alarm, silence, forget |

Question 39. If two instruments disagree, the operator should:

| A) choose the higher number always | B) verify with independent check and calibration status |
| --- | --- |
| C) choose the lower number always | D) ignore both |

Question 40. If a process change solves one issue but creates another, the operator should:

| A) stop sampling | B) hide results |
| --- | --- |
| C) balance compliance goals and reassess the whole treatment train | D) keep going blindly |

Question 41. A change in source water may require:

| A) automatic compliance | B) treatment adjustment and more monitoring |
| --- | --- |
| C) no action ever | D) lower records |

Question 42. A high TOC source may increase risk of:

| A) no taste issue | B) DBP formation |
| --- | --- |
| C) lower coagulant demand always | D) lower chlorine demand always |

Question 43. Enhanced coagulation is intended to improve:

| A) organic precursor removal for DBP control | B) pump bearing life |
| --- | --- |
| C) tank level control | D) hydrant pressure only |

Question 44. If DBPs are high in far reaches of the system, consider:

| A) only repainting tanks | B) water age, residual strategy, precursor removal, storage operation |
| --- | --- |
| C) no treatment link | D) billing routes |

Question 45. Lowering chlorine to reduce DBPs can create risk if it:

| A) increases CT always | B) compromises microbial protection/residual |
| --- | --- |
| C) removes all bacteria | D) lowers all risk |

Question 46. Switching disinfectants can affect:

| A) sample labels only | B) corrosion, nitrification, DBPs, residual stability, and monitoring needs |
| --- | --- |
| C) only color of chemical tank | D) operator grade |

Question 47. PFAS monitoring detections should lead to:

| A) no notes | B) source evaluation, communication, and treatment/regulatory planning |
| --- | --- |
| C) immediate denial | D) only chlorine increase |

Question 48. Microplastics are best treated as:

| A) an emerging, measurable concern with evolving standards and methods | B) impossible to test in any way |
| --- | --- |
| C) irrelevant forever | D) solved only by chlorine |

Question 49. A T5-level operator is expected to think in terms of:

| A) single valve only | B) no regulations |
| --- | --- |
| C) no documentation | D) system-wide risk, compliance, staff/process control, and public health |

Question 50. The final decision in a plant upset should prioritize:

| A) reducing paperwork | B) safe water and regulatory compliance over production convenience |
| --- | --- |
| C) production at all costs | D) hiding alarms |

# Answer Key - Practice Exam 05 - Scenario Judgment, Compliance, and Troubleshooting

Batch ID: T5-20260619-E05-B5325

| Q | Answer | Review |
| --- | --- | --- |
| 1 | A | source-supported with caveats |
| 2 | D | source-supported with caveats |
| 3 | A | source-supported with caveats |
| 4 | A | source-supported with caveats |
| 5 | A | source-supported with caveats |
| 6 | D | source-supported with caveats |
| 7 | D | source-supported with caveats |
| 8 | C | source-supported with caveats |
| 9 | A | source-supported with caveats |
| 10 | C | source-supported with caveats |
| 11 | C | source-supported with caveats |
| 12 | B | source-supported with caveats |
| 13 | C | source-supported with caveats |
| 14 | A | source-supported with caveats |
| 15 | A | source-supported with caveats |
| 16 | A | source-supported with caveats |
| 17 | A | source-supported with caveats |
| 18 | A | source-supported with caveats |
| 19 | B | source-supported with caveats |
| 20 | C | source-supported with caveats |
| 21 | A | source-supported with caveats |
| 22 | B | source-supported with caveats |
| 23 | C | source-supported with caveats |
| 24 | D | source-supported with caveats |
| 25 | A | source-supported with caveats |
| 26 | A | source-supported with caveats |
| 27 | C | source-supported with caveats |
| 28 | B | source-supported with caveats |
| 29 | A | source-supported with caveats |
| 30 | A | source-supported with caveats |
| 31 | A | source-supported with caveats |
| 32 | C | source-supported with caveats |
| 33 | D | source-supported with caveats |
| 34 | A | source-supported with caveats |
| 35 | B | source-supported with caveats |
| 36 | D | source-supported with caveats |
| 37 | D | source-supported with caveats |
| 38 | C | source-supported with caveats |
| 39 | B | source-supported with caveats |
| 40 | C | source-supported with caveats |
| 41 | B | source-supported with caveats |
| 42 | B | source-supported with caveats |
| 43 | A | source-supported with caveats |
| 44 | B | source-supported with caveats |
| 45 | B | source-supported with caveats |
| 46 | B | source-supported with caveats |
| 47 | B | source-supported with caveats |
| 48 | A | source-supported with caveats |
| 49 | D | source-supported with caveats |
| 50 | B | source-supported with caveats |

# T5 Math-Only Practice Bank

Batch ID: T5-20260619-E06-B1177

Question 1. A plant treats 5.0 MGD and applies chlorine at 2.0 mg/L. What is the feed in lb/day?

| A) 41.7 | B) 417 |
| --- | --- |
| C) 83.4 | D) 834 |

Question 2. A 3.5 MGD flow receives 1.5 mg/L of polymer. What is the feed in lb/day?

| A) 43.8 | B) 65.7 |
| --- | --- |
| C) 21.9 | D) 87.6 |

Question 3. A 10 MGD plant doses 25 mg/L alum. What is the feed in lb/day?

| A) 250 | B) 834 |
| --- | --- |
| C) 1,250 | D) 2,085 |

Question 4. A 2 MGD plant applies 0.8 mg/L fluoride. What is the feed in lb/day?

| A) 13.3 | B) 6.7 |
| --- | --- |
| C) 26.7 | D) 16.7 |

Question 5. A 6 MGD flow requires 3.2 mg/L chlorine. What is the feed in lb/day?

| A) 80.1 | B) 120.1 |
| --- | --- |
| C) 240.1 | D) 160.1 |

Question 6. A 4 MGD plant applies 15 mg/L coagulant. What is lb/day?

| A) 375.3 | B) 250.2 |
| --- | --- |
| C) 500.4 | D) 625.5 |

Question 7. A chemical feed rate is 100 lb/day at 2 MGD. What is the dose?

| A) 12.0 mg/L | B) 6.0 mg/L |
| --- | --- |
| C) 24.0 mg/L | D) 3.0 mg/L |

Question 8. A plant feeds 250 lb/day at 5 MGD. Approximate dose?

| A) 3.0 mg/L | B) 9.0 mg/L |
| --- | --- |
| C) 12.0 mg/L | D) 6.0 mg/L |

Question 9. A plant feeds 500 lb/day at 10 MGD. Approximate dose?

| A) 6.0 mg/L | B) 3.0 mg/L |
| --- | --- |
| C) 12.0 mg/L | D) 9.0 mg/L |

Question 10. A plant needs 200 lb/day at a dose of 4 mg/L. Approximate flow?

| A) 8 MGD | B) 2 MGD |
| --- | --- |
| C) 4 MGD | D) 6 MGD |

Question 11. A basin holds 2 MG and flow is 4 MGD. Detention time?

| A) 24 hr | B) 6 hr |
| --- | --- |
| C) 12 hr | D) 0.5 hr |

Question 12. A 1.5 MG clearwell operates at 3 MGD. Theoretical detention time?

| A) 6 hr | B) 12 hr |
| --- | --- |
| C) 24 hr | D) 18 hr |

Question 13. A 750,000 gal basin receives 2 MGD. Detention time?

| A) 12 hr | B) 6 hr |
| --- | --- |
| C) 9 hr | D) 3 hr |

Question 14. A 500,000 gal contact basin receives 1 MGD. Detention time?

| A) 24 hr | B) 6 hr |
| --- | --- |
| C) 12 hr | D) 18 hr |

Question 15. A 2.4 MG storage tank cycles at 8 MGD. Detention time?

| A) 7.2 hr | B) 14.4 hr |
| --- | --- |
| C) 3.6 hr | D) 28.8 hr |

Question 16. A basin has 1.0 MG usable volume and 2.5 MGD flow. Detention time?

| A) 6.0 hr | B) 4.8 hr |
| --- | --- |
| C) 9.6 hr | D) 12.0 hr |

Question 17. Effective contact time is 30 minutes and residual is 1.5 mg/L. CT?

| A) 45 | B) 20 |
| --- | --- |
| C) 60 | D) 30 |

Question 18. Residual is 2.2 mg/L and T10 is 25 minutes. CT?

| A) 27.5 | B) 44 |
| --- | --- |
| C) 55 | D) 75 |

Question 19. Required CT is 80. Residual is 2.0 mg/L. Required contact time?

| A) 40 min | B) 80 min |
| --- | --- |
| C) 20 min | D) 30 min |

Question 20. Required CT is 60. T10 is 30 minutes. Required residual?

| A) 2.0 mg/L | B) 1.5 mg/L |
| --- | --- |
| C) 3.0 mg/L | D) 1.0 mg/L |

Question 21. Actual CT is 54 and required CT is 48. Status?

| A) fail | B) impossible |
| --- | --- |
| C) pass | D) not enough information if values are valid |

Question 22. Actual CT is 42 and required CT is 50. Status?

| A) no concern | B) pass |
| --- | --- |
| C) exactly equal | D) fail |

Question 23. A basin has theoretical detention time 120 min and baffling factor 0.5. T10?

| A) 30 min | B) 120 min |
| --- | --- |
| C) 90 min | D) 60 min |

Question 24. A contact basin has 90 min theoretical detention and baffling factor 0.7. Effective time?

| A) 90 min | B) 70 min |
| --- | --- |
| C) 45 min | D) 63 min |

Question 25. Flow is 2 ft³/s. Convert to gpm.

| A) 449 | B) 2,000 |
| --- | --- |
| C) 898 | D) 1,388 |

Question 26. Flow is 4 ft³/s. Convert to gpm.

| A) 898 | B) 4,488 |
| --- | --- |
| C) 2,778 | D) 1,795 |

Question 27. Flow is 1.5 ft³/s. Convert to gpm.

| A) 673 | B) 1,388 |
| --- | --- |
| C) 449 | D) 337 |

Question 28. Flow is 3 MGD. Convert to gpm.

| A) 2,082 | B) 1,388 |
| --- | --- |
| C) 694 | D) 3,000 |

Question 29. Flow is 5 MGD. Convert to gpm.

| A) 3,470 | B) 2,082 |
| --- | --- |
| C) 5,000 | D) 6,940 |

Question 30. Flow is 1,388 gpm. Approximate MGD?

| A) 3 | B) 1 |
| --- | --- |
| C) 4 | D) 2 |

Question 31. A rectangular channel is 4 ft wide and 2 ft deep. Velocity is 3 ft/s. Flow?

| A) 24 ft³/s | B) 48 ft³/s |
| --- | --- |
| C) 96 ft³/s | D) 12 ft³/s |

Question 32. A pipe/channel area is 5 ft² and velocity is 2 ft/s. Flow?

| A) 5 ft³/s | B) 7 ft³/s |
| --- | --- |
| C) 20 ft³/s | D) 10 ft³/s |

Question 33. A channel flow is 16 ft³/s and area is 4 ft². Velocity?

| A) 8 ft/s | B) 2 ft/s |
| --- | --- |
| C) 16 ft/s | D) 4 ft/s |

Question 34. A channel flow is 20 ft³/s and velocity is 5 ft/s. Area?

| A) 4 ft² | B) 2 ft² |
| --- | --- |
| C) 25 ft² | D) 10 ft² |

Question 35. A tank is 40 ft long, 20 ft wide, and 10 ft deep. Volume in ft³?

| A) 80,000 | B) 10,000 |
| --- | --- |
| C) 8,000 | D) 7,000 |

Question 36. 8,000 ft³ equals approximately how many gallons?

| A) 8,340 | B) 59,840 |
| --- | --- |
| C) 80,000 | D) 748 |

Question 37. A tank contains 100,000 gal. Approximate weight of water?

| A) 834,000 lb | B) 1,000,000 lb |
| --- | --- |
| C) 748,000 lb | D) 100,000 lb |

Question 38. A tank contains 1 MG. Approximate weight of water?

| A) 8.34 million lb | B) 0.834 million lb |
| --- | --- |
| C) 1 million lb | D) 83.4 million lb |

Question 39. Pressure is 50 psi. Head?

| A) 231 ft | B) 115.5 ft |
| --- | --- |
| C) 50 ft | D) 21.7 ft |

Question 40. Pressure is 80 psi. Head?

| A) 80 ft | B) 184.8 ft |
| --- | --- |
| C) 34.6 ft | D) 231 ft |

Question 41. Head is 100 ft. Pressure?

| A) 23 psi | B) 231 psi |
| --- | --- |
| C) 43 psi | D) 100 psi |

Question 42. Head is 200 ft. Pressure?

| A) 100 psi | B) 200 psi |
| --- | --- |
| C) 87 psi | D) 43 psi |

Question 43. Elevation difference is 300 ft. Static pressure at bottom?

| A) 130 psi | B) 60 psi |
| --- | --- |
| C) 300 psi | D) 30 psi |

Question 44. A pump lifts water 150 ft and discharge pressure is equivalent to 100 ft. Ignoring losses, total head?

| A) 250 ft | B) 300 ft |
| --- | --- |
| C) 50 ft | D) 150 ft |

Question 45. Static lift is 80 ft, friction loss is 20 ft, and pressure head is 100 ft. TDH?

| A) 200 ft | B) 220 ft |
| --- | --- |
| C) 180 ft | D) 100 ft |

Question 46. A pump delivers 1,000 gpm against 200 ft head. Water horsepower is approximately gpm × head ÷ 3960. WHP?

| A) 101.0 | B) 75.8 |
| --- | --- |
| C) 25.3 | D) 50.5 |

Question 47. If water horsepower is 50 and pump efficiency is 75%, brake horsepower needed?

| A) 66.7 | B) 50 |
| --- | --- |
| C) 37.5 | D) 75 |

Question 48. A motor draws 80 BHP and produces 60 WHP. Efficiency?

| A) 60% | B) 80% |
| --- | --- |
| C) 75% | D) 70% |

Question 49. A pump runs 12 hr/day at 500 gpm. Daily volume?

| A) 0.18 MG | B) 0.36 MG |
| --- | --- |
| C) 0.72 MG | D) 1.44 MG |

Question 50. A pump runs 24 hr/day at 1,000 gpm. Daily volume?

| A) 0.694 MG | B) 1.0 MG |
| --- | --- |
| C) 2.0 MG | D) 1.44 MG |

Question 51. A filter is 20 ft by 30 ft. Area?

| A) 50 ft² | B) 600 ft² |
| --- | --- |
| C) 900 ft² | D) 300 ft² |

Question 52. A filter treats 1,800 gpm and has 600 ft² area. Loading rate?

| A) 2 gpm/ft² | B) 3 gpm/ft² |
| --- | --- |
| C) 1 gpm/ft² | D) 6 gpm/ft² |

Question 53. Filter area is 500 ft² and loading rate is 4 gpm/ft². Flow?

| A) 2,000 gpm | B) 1,000 gpm |
| --- | --- |
| C) 2,500 gpm | D) 1,500 gpm |

Question 54. A filter treats 2 MGD with 700 ft² area. Approximate loading rate?

| A) 2 gpm/ft² | B) 3 gpm/ft² |
| --- | --- |
| C) 1 gpm/ft² | D) 4 gpm/ft² |

Question 55. Backwash rate is 15 gpm/ft² and filter area is 600 ft². Backwash flow?

| A) 9,000 gpm | B) 15,000 gpm |
| --- | --- |
| C) 6,000 gpm | D) 12,000 gpm |

Question 56. Backwash flow is 8,000 gpm for 10 minutes. Volume?

| A) 80,000 gal | B) 40,000 gal |
| --- | --- |
| C) 8,000 gal | D) 800,000 gal |

Question 57. A sedimentation basin has flow 4 MGD and surface area 8,000 ft². Overflow rate?

| A) 250 gpd/ft² | B) 500 gpd/ft² |
| --- | --- |
| C) 750 gpd/ft² | D) 1,000 gpd/ft² |

Question 58. Flow is 6 MGD and basin surface area is 12,000 ft². Overflow rate?

| A) 1,000 gpd/ft² | B) 750 gpd/ft² |
| --- | --- |
| C) 250 gpd/ft² | D) 500 gpd/ft² |

Question 59. A clarifier weir is 200 ft long and flow is 4 MGD. Weir loading?

| A) 40,000 gpd/ft | B) 20,000 gpd/ft |
| --- | --- |
| C) 30,000 gpd/ft | D) 10,000 gpd/ft |

Question 60. Weir length is 300 ft and flow is 6 MGD. Weir loading?

| A) 30,000 gpd/ft | B) 10,000 gpd/ft |
| --- | --- |
| C) 20,000 gpd/ft | D) 40,000 gpd/ft |

Question 61. A solution is 10% strength. As a decimal, that is:

| A) 0.01 | B) 10 |
| --- | --- |
| C) 0.10 | D) 1.0 |

Question 62. A 12.5% hypochlorite solution has what decimal strength?

| A) 0.0125 | B) 1.25 |
| --- | --- |
| C) 0.125 | D) 12.5 |

Question 63. A chemical pump delivers 2 gal/hr. How many gallons per day if run continuously?

| A) 36 | B) 24 |
| --- | --- |
| C) 48 | D) 60 |

Question 64. A feed pump delivers 0.5 gal/min. Gallons per day?

| A) 2,880 | B) 5,000 |
| --- | --- |
| C) 1,440 | D) 720 |

Question 65. A chemical tank drops 30 gallons in 6 hours. Feed rate?

| A) 5 gph | B) 30 gph |
| --- | --- |
| C) 3 gph | D) 6 gph |

Question 66. A tank drops 12 inches in a uniform tank where each inch equals 5 gallons. Volume used?

| A) 50 gal | B) 120 gal |
| --- | --- |
| C) 60 gal | D) 17 gal |

Question 67. Chemical used is 80 gallons over 24 hours. Feed rate?

| A) 3.3 gph | B) 2.5 gph |
| --- | --- |
| C) 4.8 gph | D) 1.7 gph |

Question 68. A 500-gallon chemical tank uses 125 gallons. Percent remaining?

| A) 50% | B) 75% |
| --- | --- |
| C) 25% | D) 80% |

Question 69. A sample result is 0.080 mg/L. In µg/L, this is:

| A) 80 | B) 800 |
| --- | --- |
| C) 0.080 | D) 8 |

Question 70. A result is 4 ng/L. In ppt for water, this is approximately:

| A) 4 ppt | B) 0.4 ppt |
| --- | --- |
| C) 40 ppt | D) 400 ppt |

Question 71. 10 mg/L equals:

| A) 10,000 µg/L | B) 1,000 µg/L |
| --- | --- |
| C) 100 µg/L | D) 10 µg/L |

Question 72. 1 µg/L equals:

| A) 100 ng/L | B) 1,000 ng/L |
| --- | --- |
| C) 1 ng/L | D) 10 ng/L |

Question 73. A pH change from 7 to 6 means hydrogen ion concentration is:

| A) 10 times higher | B) 10 times lower |
| --- | --- |
| C) unchanged | D) 2 times higher |

Question 74. A disinfectant residual decreases from 2.0 to 1.0 mg/L. Percent decrease?

| A) 25% | B) 75% |
| --- | --- |
| C) 100% | D) 50% |

Question 75. Turbidity goes from 0.20 NTU to 0.30 NTU. Increase?

| A) 150% | B) 25% |
| --- | --- |
| C) 100% | D) 50% |

Question 76. A chemical dose increases from 20 to 25 mg/L. Percent increase?

| A) 20% | B) 50% |
| --- | --- |
| C) 25% | D) 5% |

Question 77. A 1,000 mL sample is the same as:

| A) 0.1 L | B) 100 L |
| --- | --- |
| C) 1 L | D) 10 L |

Question 78. A 250 mL sample is what fraction of a liter?

| A) 2.5 L | B) 0.25 L |
| --- | --- |
| C) 25 L | D) 0.025 L |

Question 79. A 100 mL sample contains 20 colonies. Result per 100 mL?

| A) 20 | B) 2,000 |
| --- | --- |
| C) 200 | D) 2 |

Question 80. A 500 mL sample contains 5 particles. Equivalent per liter?

| A) 5 | B) 2.5 |
| --- | --- |
| C) 50 | D) 10 |

Question 81. Chlorine demand is the difference between:

| A) turbidity and color | B) dose and residual |
| --- | --- |
| C) pH and alkalinity | D) flow and volume |

Question 82. Chlorine dose is 3.0 mg/L and residual is 1.2 mg/L. Demand?

| A) 4.2 | B) 1.8 |
| --- | --- |
| C) 1.2 | D) 3.0 |

Question 83. Chlorine demand is 2.5 mg/L and residual target is 1.0 mg/L. Dose needed?

| A) 2.5 | B) 3.5 |
| --- | --- |
| C) 1.5 | D) 4.5 |

Question 84. Applied dose is 4 mg/L and demand is 1.5 mg/L. Residual?

| A) 5.5 | B) 4.0 |
| --- | --- |
| C) 2.5 | D) 1.5 |

Question 85. A tank has diameter 40 ft and water depth 20 ft. Using 0.785 × D² × depth, volume ft³?

| A) 62,800 | B) 25,120 |
| --- | --- |
| C) 31,400 | D) 12,560 |

Question 86. 25,120 ft³ equals gallons?

| A) 100,000 | B) 187,898 |
| --- | --- |
| C) 250,000 | D) 25,120 |

Question 87. A circular tank diameter doubles. Surface area changes by:

| A) 2x | B) 4x |
| --- | --- |
| C) 8x | D) 3x |

Question 88. A rectangular basin is 100 ft × 50 ft × 12 ft. Volume gallons?

| A) 600,000 | B) 224,400 |
| --- | --- |
| C) 448,800 | D) 60,000 |

Question 89. A basin contains 448,800 gallons and flow is 1,496 gpm. Detention time?

| A) 450 min | B) 300 min |
| --- | --- |
| C) 150 min | D) 600 min |

Question 90. A flow of 1,496 gpm is approximately:

| A) 1.50 MGD | B) 1.08 MGD |
| --- | --- |
| C) 3.0 MGD | D) 2.15 MGD |

Question 91. A well pumps 700 gpm. Approximate MGD?

| A) 1.5 | B) 1.0 |
| --- | --- |
| C) 0.5 | D) 2.0 |

Question 92. Three pumps each deliver 2 MGD. Total firm capacity with largest pump out?

| A) 2 MGD | B) 6 MGD |
| --- | --- |
| C) 4 MGD | D) 8 MGD |

Question 93. Demand is 5 MGD. Firm capacity is 4 MGD. Deficit?

| A) 1 MGD | B) 4 MGD |
| --- | --- |
| C) 5 MGD | D) 2 MGD |

Question 94. Storage is 10 MG and average demand is 5 MGD. Storage equals:

| A) 1 day | B) 10 days |
| --- | --- |
| C) 2 days | D) 5 days |

Question 95. Peak flow is 12 MGD and average flow is 6 MGD. Peaking factor?

| A) 2.0 | B) 6.0 |
| --- | --- |
| C) 0.5 | D) 12.0 |

Question 96. A plant produces 7 MG and bills 6.3 MG. Apparent/real loss combined?

| A) 90% | B) 10% |
| --- | --- |
| C) 20% | D) 5% |

Question 97. A chemical costs $2.50/lb and usage is 400 lb/day. Daily cost?

| A) $1,000 | B) $4,000 |
| --- | --- |
| C) $500 | D) $100 |

Question 98. Energy use is 1,200 kWh/day at $0.20/kWh. Daily cost?

| A) $1,200 | B) $120 |
| --- | --- |
| C) $240 | D) $200 |

Question 99. A motor runs 20 hr at 50 kW. Energy used?

| A) 2,000 kWh | B) 500 kWh |
| --- | --- |
| C) 10,000 kWh | D) 1,000 kWh |

Question 100. A process removes turbidity from 10 NTU to 0.5 NTU. Percent removal?

| A) 50% | B) 90% |
| --- | --- |
| C) 99% | D) 95% |

# Answer Key - T5 Math-Only Practice Bank

Batch ID: T5-20260619-E06-B1177

| Q | Answer | Review |
| --- | --- | --- |
| 1 | C | source-supported with caveats |
| 2 | A | source-supported with caveats |
| 3 | D | source-supported with caveats |
| 4 | A | source-supported with caveats |
| 5 | D | source-supported with caveats |
| 6 | C | source-supported with caveats |
| 7 | B | source-supported with caveats |
| 8 | D | source-supported with caveats |
| 9 | A | source-supported with caveats |
| 10 | D | source-supported with caveats |
| 11 | C | source-supported with caveats |
| 12 | B | source-supported with caveats |
| 13 | C | source-supported with caveats |
| 14 | C | source-supported with caveats |
| 15 | A | source-supported with caveats |
| 16 | C | source-supported with caveats |
| 17 | A | source-supported with caveats |
| 18 | C | source-supported with caveats |
| 19 | A | source-supported with caveats |
| 20 | A | source-supported with caveats |
| 21 | C | source-supported with caveats |
| 22 | D | source-supported with caveats |
| 23 | D | source-supported with caveats |
| 24 | D | source-supported with caveats |
| 25 | C | source-supported with caveats |
| 26 | D | source-supported with caveats |
| 27 | A | source-supported with caveats |
| 28 | A | source-supported with caveats |
| 29 | A | source-supported with caveats |
| 30 | D | source-supported with caveats |
| 31 | A | source-supported with caveats |
| 32 | D | source-supported with caveats |
| 33 | D | source-supported with caveats |
| 34 | A | source-supported with caveats |
| 35 | C | source-supported with caveats |
| 36 | B | source-supported with caveats |
| 37 | A | source-supported with caveats |
| 38 | A | source-supported with caveats |
| 39 | B | source-supported with caveats |
| 40 | B | source-supported with caveats |
| 41 | C | source-supported with caveats |
| 42 | C | source-supported with caveats |
| 43 | A | source-supported with caveats |
| 44 | A | source-supported with caveats |
| 45 | A | source-supported with caveats |
| 46 | D | source-supported with caveats |
| 47 | A | source-supported with caveats |
| 48 | C | source-supported with caveats |
| 49 | B | source-supported with caveats |
| 50 | D | source-supported with caveats |
| 51 | B | source-supported with caveats |
| 52 | B | source-supported with caveats |
| 53 | A | source-supported with caveats |
| 54 | A | source-supported with caveats |
| 55 | A | source-supported with caveats |
| 56 | A | source-supported with caveats |
| 57 | B | source-supported with caveats |
| 58 | D | source-supported with caveats |
| 59 | B | source-supported with caveats |
| 60 | C | source-supported with caveats |
| 61 | C | source-supported with caveats |
| 62 | C | source-supported with caveats |
| 63 | C | source-supported with caveats |
| 64 | D | source-supported with caveats |
| 65 | A | source-supported with caveats |
| 66 | C | source-supported with caveats |
| 67 | A | source-supported with caveats |
| 68 | B | source-supported with caveats |
| 69 | A | source-supported with caveats |
| 70 | A | source-supported with caveats |
| 71 | A | source-supported with caveats |
| 72 | B | source-supported with caveats |
| 73 | A | source-supported with caveats |
| 74 | D | source-supported with caveats |
| 75 | D | source-supported with caveats |
| 76 | C | source-supported with caveats |
| 77 | C | source-supported with caveats |
| 78 | B | source-supported with caveats |
| 79 | A | source-supported with caveats |
| 80 | D | source-supported with caveats |
| 81 | B | source-supported with caveats |
| 82 | B | source-supported with caveats |
| 83 | B | source-supported with caveats |
| 84 | C | source-supported with caveats |
| 85 | B | source-supported with caveats |
| 86 | B | source-supported with caveats |
| 87 | B | source-supported with caveats |
| 88 | C | source-supported with caveats |
| 89 | B | source-supported with caveats |
| 90 | D | source-supported with caveats |
| 91 | B | source-supported with caveats |
| 92 | C | source-supported with caveats |
| 93 | A | source-supported with caveats |
| 94 | C | source-supported with caveats |
| 95 | A | source-supported with caveats |
| 96 | B | source-supported with caveats |
| 97 | A | source-supported with caveats |
| 98 | C | source-supported with caveats |
| 99 | D | source-supported with caveats |
| 100 | D | source-supported with caveats |

# T5 PFAS and Emerging Contaminants Mini Exam

Batch ID: T5-20260619-E07-B2715

Question 1. PFAS stands for:

| A) primary filtration and sedimentation | B) public fluoride assessment standard |
| --- | --- |
| C) pressure-flow adjustment system | D) per- and polyfluoroalkyl substances |

Question 2. PFAS are often called forever chemicals because they are generally:

| A) only found in chlorine | B) persistent and resistant to breakdown |
| --- | --- |
| C) always radioactive | D) living organisms |

Question 3. PFOA stands for:

| A) perfluorooctanoic acid | B) primary fluoride organic analyte |
| --- | --- |
| C) polyfilter oxidation agent | D) potable finished ozone acid |

Question 4. PFOS stands for:

| A) perfluorooctane sulfonic acid | B) primary fluoride ozone scale |
| --- | --- |
| C) public finished organic solids | D) pressure filtration operating standard |

Question 5. A common historical source category for PFAS contamination is:

| A) firefighting foam and industrial uses | B) natural limestone only |
| --- | --- |
| C) chlorine gas only | D) filter sand only |

Question 6. PFAS may also be associated with:

| A) only ozone feed | B) only copper pipe |
| --- | --- |
| C) only volcanic rock | D) stain-resistant, nonstick, waterproof, and grease-resistant products |

Question 7. A common analytical approach for select PFAS in drinking water is:

| A) settleometer only | B) pH paper only |
| --- | --- |
| C) LC-MS/MS methods such as EPA Method 533 or 537.1 | D) visual color wheel only |

Question 8. In drinking-water PFAS reporting, ppt is commonly equivalent to:

| A) mg/L | B) psi |
| --- | --- |
| C) ng/L | D) gpm |

Question 9. 4 ppt is equivalent to:

| A) 4 mg/L | B) 4 gpm |
| --- | --- |
| C) 4 ng/L | D) 4 NTU |

Question 10. 1 µg/L equals:

| A) 100 ng/L | B) 1 ng/L |
| --- | --- |
| C) 1,000 ng/L | D) 10 ng/L |

Question 11. EPA's 2024 final PFAS NPDWR listed PFOA and PFOS enforceable MCLs as:

| A) 0.080 mg/L each | B) 1 NTU each |
| --- | --- |
| C) 4 ppt each | D) 10 mg/L each |

Question 12. EPA's 2024 final rule used a Hazard Index concept for certain PFAS mixtures involving:

| A) nitrate and nitrite only | B) Giardia and viruses only |
| --- | --- |
| C) PFHxS, PFNA, HFPO-DA/GenX, and PFBS | D) lead and copper only |

Question 13. A Maximum Contaminant Level Goal is:

| A) a required sample bottle size | B) always the same as a public notice deadline |
| --- | --- |
| C) a pump speed | D) non-enforceable health-based goal |

Question 14. An MCL is:

| A) only a lab method | B) legally enforceable contaminant limit |
| --- | --- |
| C) only a recommended taste level | D) a pipe pressure target |

Question 15. California notification levels are best understood as:

| A) health-based advisory levels for chemicals without state MCLs | B) pump alarms |
| --- | --- |
| C) lab invoices | D) federal permits only |

Question 16. A California response level generally indicates:

| A) a customer billing class | B) a chlorine contact basin volume |
| --- | --- |
| C) a level where source removal, treatment, blending, or public notification may be recommended/required depending on rule context | D) a filter backwash rate |

Question 17. If PFAS are detected above an applicable response level, the operator/system should:

| A) ignore because PFAS are invisible | B) flush one hydrant and close the case |
| --- | --- |
| C) increase fluoride only | D) follow DDW direction, evaluate source use/treatment/blending, and handle required notification |

Question 18. The best operator response to a PFAS detection is:

| A) change unrelated pump bearings | B) assume lab error without review |
| --- | --- |
| C) verify data quality, identify affected source/sample point, coordinate with compliance staff/regulator, and plan response | D) hide the result |

Question 19. PFAS sampling requires special care because:

| A) pH strips are enough | B) samples can be collected in any food container |
| --- | --- |
| C) cross-contamination from common materials can affect low-level results | D) chlorine residual destroys PFAS immediately |

Question 20. Examples of PFAS sampling contamination sources can include:

| A) only stainless steel pipes | B) certain waterproof clothing, cosmetics, food wrappers, or PTFE-containing materials |
| --- | --- |
| C) only turbidity standards | D) only glass bottles |

Question 21. PFAS treatment commonly includes:

| A) granular activated carbon, ion exchange, and reverse osmosis/nanofiltration | B) sedimentation alone |
| --- | --- |
| C) standard chlorination alone | D) fluoridation alone |

Question 22. GAC removes many PFAS primarily by:

| A) gravity settling | B) converting them to chlorine |
| --- | --- |
| C) adsorption | D) UV color change |

Question 23. Ion exchange removes PFAS by:

| A) exchange/sorption on engineered resin | B) boiling water |
| --- | --- |
| C) hydrant flushing only | D) pH paper |

Question 24. Reverse osmosis removes PFAS by:

| A) corrosion coupons | B) pressure-driven membrane separation |
| --- | --- |
| C) floc blanket settling only | D) chlorine demand |

Question 25. A key operational concern for GAC PFAS treatment is:

| A) fluoride color | B) hydrant caps |
| --- | --- |
| C) media breakthrough and replacement/regeneration planning | D) tank altitude only |

Question 26. A key operational concern for ion exchange PFAS treatment is:

| A) jar-test paddles only | B) resin exhaustion, selectivity, regeneration/disposal issues |
| --- | --- |
| C) chlorine gas pressure | D) finished-water temperature only |

Question 27. A key operational concern for RO PFAS treatment is:

| A) backflow testing only | B) pH meter color |
| --- | --- |
| C) filter-to-waste only | D) concentrate disposal and membrane management |

Question 28. Standard chlorine disinfection is generally:

| A) enough to remove all forever chemicals | B) not considered a primary PFAS removal method |
| --- | --- |
| C) the best PFAS destruction method in distribution | D) required to convert PFAS to lead |

Question 29. Blending may reduce delivered concentration but:

| A) destroys PFAS chemically | B) does not destroy or remove the contaminant mass |
| --- | --- |
| C) works without compliance review | D) eliminates monitoring need |

Question 30. Source substitution can be useful when:

| A) no regulator coordination is needed | B) another approved source has lower contaminant levels and capacity is available |
| --- | --- |
| C) all sources have identical chemistry | D) the contaminated source is the only source |

Question 31. A T5-level PFAS decision should consider:

| A) only pump color | B) only taste |
| --- | --- |
| C) only daily production target | D) public health, compliance, source capacity, treatment feasibility, residuals, waste streams, and communication |

Question 32. PFAS compounds differ from each other in:

| A) chain length, functional group, mobility, treatability, and toxicity data | B) only color |
| --- | --- |
| C) only spelling | D) only pH |

Question 33. Short-chain PFAS can be harder for some adsorptive media because they may be:

| A) more mobile and less strongly adsorbed | B) destroyed by visible light |
| --- | --- |
| C) easier to settle by gravity | D) converted to turbidity |

Question 34. PFHxS is:

| A) a pipe valve | B) a turbidity method |
| --- | --- |
| C) a PFAS compound | D) a bacterium |

Question 35. PFNA is:

| A) a pump bearing | B) a PFAS compound |
| --- | --- |
| C) nitrate as nitrogen | D) a disinfectant residual |

Question 36. HFPO-DA / GenX is:

| A) a replacement PFAS associated with fluoropolymer manufacturing | B) a storage tank coating inspection only |
| --- | --- |
| C) a filter media size | D) a coliform test |

Question 37. PFBS is:

| A) a shorter-chain PFAS included in certain mixture/hazard-index discussions | B) a chlorine residual |
| --- | --- |
| C) a pressure unit | D) a bacteriological sample type |

Question 38. Microplastics are generally defined as:

| A) dissolved oxygen | B) chlorine residual |
| --- | --- |
| C) nitrate ion | D) small plastic particles, often discussed from 5 mm down to very small particles |

Question 39. Nanoplastics are generally:

| A) equivalent to PFOS | B) larger than gravel |
| --- | --- |
| C) smaller plastic particles below the microplastic range | D) always visible to the eye |

Question 40. Microplastics are a real issue because they are:

| A) measurable and under active health/method-development research | B) removed only by chlorine |
| --- | --- |
| C) imaginary and untestable | D) created only by operators |

Question 41. A key microplastics challenge is:

| A) lack of one simple standardized routine method for all particle sizes and polymers | B) no environmental presence |
| --- | --- |
| C) immediate acute MCL exceedance in all systems | D) impossibility of any lab observation |

Question 42. Treatment processes that may reduce particles, including some microplastics, can include:

| A) pressure gauges only | B) billing software |
| --- | --- |
| C) coagulation, sedimentation, filtration, membrane processes | D) fluoride only |

Question 43. Microplastics should be discussed carefully because:

| A) they are the same as Giardia | B) they are not particles |
| --- | --- |
| C) the science is real but risk, methods, and regulation are still developing | D) they are already fully regulated like nitrate everywhere |

Question 44. Cyanotoxins are associated with:

| A) cross-connection assemblies | B) harmful algal blooms/cyanobacteria |
| --- | --- |
| C) copper service lines only | D) pump cavitation |

Question 45. Common cyanotoxins of drinking-water concern include:

| A) PFOA and PFOS only | B) microcystins, cylindrospermopsin, anatoxin-a, and saxitoxin |
| --- | --- |
| C) lead and copper only | D) hardness and alkalinity only |

Question 46. Cyanotoxin response may require:

| A) source monitoring, treatment optimization, public-health coordination, and communication | B) stopping samples |
| --- | --- |
| C) ignoring reservoir blooms | D) lowering all coagulant |

Question 47. 1,4-dioxane is commonly considered:

| A) a pressure unit | B) a disinfectant residual |
| --- | --- |
| C) an emerging/unregulated contaminant of concern in some contexts | D) a filter loading rate |

Question 48. Perchlorate is important because it affects:

| A) tank level | B) pump vibration |
| --- | --- |
| C) turbidity calibration only | D) thyroid-related health concerns and has drinking-water regulatory history |

Question 49. An operator should describe emerging contaminants as:

| A) contaminants with evolving occurrence, health, method, or regulatory status | B) always treated by chlorine |
| --- | --- |
| C) fake contaminants | D) always unmeasurable |

Question 50. The most exam-safe attitude toward PFAS and emerging contaminants is:

| A) treat all as identical | B) memorize social-media claims |
| --- | --- |
| C) know current regulated/advisory status, detection methods, likely sources, treatment options, and communication duties | D) assume no monitoring applies |

# Answer Key - T5 PFAS and Emerging Contaminants Mini Exam

Batch ID: T5-20260619-E07-B2715

| Q | Answer | Review |
| --- | --- | --- |
| 1 | D | source-supported with caveats |
| 2 | B | source-supported with caveats |
| 3 | A | source-supported with caveats |
| 4 | A | source-supported with caveats |
| 5 | A | source-supported with caveats |
| 6 | D | source-supported with caveats |
| 7 | C | source-supported with caveats |
| 8 | C | source-supported with caveats |
| 9 | C | source-supported with caveats |
| 10 | C | source-supported with caveats |
| 11 | C | source-supported with caveats |
| 12 | C | source-supported with caveats |
| 13 | D | source-supported with caveats |
| 14 | B | source-supported with caveats |
| 15 | A | source-supported with caveats |
| 16 | C | source-supported with caveats |
| 17 | D | source-supported with caveats |
| 18 | C | source-supported with caveats |
| 19 | C | source-supported with caveats |
| 20 | B | source-supported with caveats |
| 21 | A | source-supported with caveats |
| 22 | C | source-supported with caveats |
| 23 | A | source-supported with caveats |
| 24 | B | source-supported with caveats |
| 25 | C | source-supported with caveats |
| 26 | B | source-supported with caveats |
| 27 | D | source-supported with caveats |
| 28 | B | source-supported with caveats |
| 29 | B | source-supported with caveats |
| 30 | B | source-supported with caveats |
| 31 | D | source-supported with caveats |
| 32 | A | source-supported with caveats |
| 33 | A | source-supported with caveats |
| 34 | C | source-supported with caveats |
| 35 | B | source-supported with caveats |
| 36 | A | source-supported with caveats |
| 37 | A | source-supported with caveats |
| 38 | D | source-supported with caveats |
| 39 | C | source-supported with caveats |
| 40 | A | source-supported with caveats |
| 41 | A | source-supported with caveats |
| 42 | C | source-supported with caveats |
| 43 | C | source-supported with caveats |
| 44 | B | source-supported with caveats |
| 45 | B | source-supported with caveats |
| 46 | A | source-supported with caveats |
| 47 | C | source-supported with caveats |
| 48 | D | source-supported with caveats |
| 49 | A | source-supported with caveats |
| 50 | C | source-supported with caveats |

# T5 Practice Exam 06 - Advanced Scenario Mix

Batch ID: T5-20260619-E08-B6332

Question 1. A plant has rising raw turbidity, falling alkalinity, and poorer settled-water turbidity after a storm. Best first operating focus?

| A) reassess coagulation chemistry and jar-test/adjust dose and pH control | B) lower all chemical feed |
| --- | --- |
| C) stop all monitoring | D) ignore because filters will fix it |

Question 2. Finished water turbidity is still below the regulatory maximum but trending upward across multiple filters. Best response?

| A) disable alarms | B) only notify customers |
| --- | --- |
| C) investigate before a limit is reached | D) wait for a violation |

Question 3. One filter shows turbidity spikes after every backwash while others do not. Most likely review area?

| A) that filter's backwash/ripening/media/underdrain condition | B) CCR mailing list |
| --- | --- |
| C) source nitrate only | D) tank altitude |

Question 4. Coagulant dose is increased and settled turbidity improves, but finished pH drops near the lower corrosion-control target. Best next step?

| A) ignore pH | B) keep increasing dose only |
| --- | --- |
| C) balance coagulation with alkalinity/pH control | D) stop corrosion monitoring |

Question 5. A chlorine analyzer shows low residual, but grab samples at the same point are normal. Best action?

| A) shut down all treatment | B) increase chlorine until analyzer rises |
| --- | --- |
| C) assume water is unsafe without verification | D) troubleshoot analyzer while maintaining verified manual checks |

Question 6. A low clearwell level during peak demand threatens CT. Best operational concern?

| A) contact time may be reduced and compliance margin may shrink | B) pH always rises |
| --- | --- |
| C) water gets heavier | D) turbidity always drops |

Question 7. If CT is failing, the operator should evaluate:

| A) residual, T10/contact time, pH, temperature, and flow | B) only payroll |
| --- | --- |
| C) only fluoride feed | D) only tank paint |

Question 8. A source has PFAS detections above an applicable response level. Best system response?

| A) chlorinate harder | B) coordinate with regulator, evaluate treatment/blending/source removal, and handle required notification |
| --- | --- |
| C) flush dead ends only | D) ignore until customers ask |

Question 9. A PFAS sample may be invalid if:

| A) it was cold | B) it was labeled |
| --- | --- |
| C) sampling contamination or improper materials compromised the sample | D) it was analyzed by LC-MS/MS |

Question 10. A new source has lower PFAS but higher manganese. Best T5-level thinking?

| A) ignore manganese | B) switch immediately without evaluation |
| --- | --- |
| C) compare whole-water-quality impacts, treatment needs, compliance, and customer effects | D) choose based only on distance |

Question 11. A main break causes low pressure and muddy water complaints. Best priority?

| A) restore aesthetics only | B) assume no intrusion |
| --- | --- |
| C) delay records | D) protect public health: isolate, repair, flush, disinfect/sample, and notify as required |

Question 12. A storage tank hatch is found unsecured. Best response?

| A) assess sanitary breach, secure site, coordinate sampling/disinfection/notification as needed | B) close it and say nothing |
| --- | --- |
| C) increase fluoride | D) repaint tank |

Question 13. A distribution residual is low at a far dead end. Possible causes include:

| A) water age, demand, nitrification, biofilm, or inadequate turnover | B) lower risk |
| --- | --- |
| C) better disinfection | D) lower customer count only |

Question 14. Chloraminated system shows falling total chlorine, rising nitrite, and low free ammonia control. Suspect:

| A) arsenic precipitation | B) filter ripening |
| --- | --- |
| C) PFAS breakthrough | D) nitrification |

Question 15. A nitrification response plan may include:

| A) no samples | B) stopping all chlorine |
| --- | --- |
| C) increasing water age | D) flushing, residual management, ammonia control, storage turnover, and monitoring |

Question 16. DBP results are high in distant parts of the system. Likely contributing factor?

| A) too little contact time only | B) no organic matter ever |
| --- | --- |
| C) high water age and precursor/residual interaction | D) pump cavitation |

Question 17. Reducing chlorine to control DBPs can create risk if it:

| A) removes organics | B) eliminates sampling |
| --- | --- |
| C) compromises microbial protection | D) lowers all risk |

Question 18. Enhanced coagulation is used primarily to:

| A) reduce lead service lines directly | B) increase pump head |
| --- | --- |
| C) disinfect tanks | D) improve removal of DBP precursors |

Question 19. Algae bloom in reservoir creates taste/odor complaints. Best response?

| A) turn off filters | B) billing adjustment only |
| --- | --- |
| C) no action | D) source monitoring plus treatment adjustment such as oxidation/adsorption/coagulation strategy |

Question 20. Cyanotoxin concern should trigger:

| A) lower sampling | B) no treatment review |
| --- | --- |
| C) monitoring and public-health/regulatory coordination | D) routine odor note only |

Question 21. A chemical delivery arrives for the wrong tank connection. Best action?

| A) stop unloading until chemical/tank/connection are verified | B) unload quickly |
| --- | --- |
| C) let driver decide alone | D) dilute with water |

Question 22. Hypochlorite mixed with acid can release:

| A) oxygen only | B) chlorine gas |
| --- | --- |
| C) fluoride | D) sand |

Question 23. A caustic feed pump sticks on and pH rises rapidly. Best response?

| A) isolate/control feed, verify pH, protect treatment/distribution, and document | B) disable pH analyzer |
| --- | --- |
| C) ignore if water is clear | D) add acid blindly without procedure |

Question 24. A coagulant feed failure during high turbidity can quickly affect:

| A) clarification/filter performance and finished water turbidity | B) fluoride MCL |
| --- | --- |
| C) tank coating | D) customer billing only |

Question 25. A filter is producing acceptable turbidity but particle counts are rising. Best T5 interpretation?

| A) early warning may indicate performance change before turbidity limit | B) filter is perfect |
| --- | --- |
| C) no need to investigate | D) particle counts never matter |

Question 26. A membrane integrity failure indicates:

| A) potential barrier compromise | B) more alkalinity |
| --- | --- |
| C) lower PFAS | D) stronger chlorine |

Question 27. RO treatment for PFAS requires planning for:

| A) hydrant flushing | B) concentrate handling |
| --- | --- |
| C) jar-test paddles | D) chlorine residual only |

Question 28. GAC breakthrough means:

| A) tank has air gap | B) contaminant is passing through as media capacity is exhausted |
| --- | --- |
| C) pH is too low only | D) media is brand new |

Question 29. Ion exchange resin exhaustion can cause:

| A) lower water age | B) instant disinfection |
| --- | --- |
| C) target contaminant leakage/breakthrough | D) more CT |

Question 30. A lab reports an unexpected contaminant detection just above an MCL. First step?

| A) publicly announce without review | B) ignore unless customer complains |
| --- | --- |
| C) delete sample | D) verify result, sample details, compliance basis, and required response |

Question 31. A monitoring violation means:

| A) pump failed | B) required monitoring/reporting was missed or invalid |
| --- | --- |
| C) contaminant always exceeded health limit | D) source dried up |

Question 32. A treatment technique violation means:

| A) only a late bill | B) required process/control was not met |
| --- | --- |
| C) only a customer complaint | D) all water is automatically safe |

Question 33. Public notification timing depends mainly on:

| A) weather | B) operator preference |
| --- | --- |
| C) tank size | D) risk/violation tier and regulatory requirements |

Question 34. A Tier 1 situation generally indicates:

| A) no health concern | B) annual routine notice only |
| --- | --- |
| C) billing update | D) urgent potential health risk requiring rapid notice |

Question 35. A Consumer Confidence Report is:

| A) daily pump log | B) chemical SDS |
| --- | --- |
| C) filter inspection sheet | D) annual customer water quality report |

Question 36. A SCADA trend shows pump amps slowly increasing over weeks. Best use of this trend?

| A) increase chlorine | B) delete history |
| --- | --- |
| C) ignore until trip | D) plan inspection/maintenance before failure |

Question 37. Pump cavitation can damage:

| A) coagulant only | B) impellers and pump components |
| --- | --- |
| C) CCRs | D) sample bottles |

Question 38. Water hammer can be reduced by:

| A) ignoring air valves | B) faster valve closures |
| --- | --- |
| C) controlled valve operation, surge protection, and pump control | D) lowering all residual |

Question 39. Lockout/tagout protects workers from:

| A) taste and odor | B) microplastics |
| --- | --- |
| C) nitrate | D) hazardous energy |

Question 40. Confined-space entry should occur only after:

| A) no paperwork | B) lone entry |
| --- | --- |
| C) hazard evaluation, atmospheric testing, controls, and permit/procedure as applicable | D) a quick look |

Question 41. A good emergency response plan includes:

| A) only old phone numbers | B) no public communication |
| --- | --- |
| C) no maps | D) roles, contacts, alternatives, communication, and exercises |

Question 42. Mutual aid is useful because it can provide:

| A) no documentation | B) staff, equipment, supplies, or operational support during emergencies |
| --- | --- |
| C) automatic MCL waivers | D) lower DBPs directly |

Question 43. A vulnerability assessment helps identify:

| A) filter loading only | B) finished pH |
| --- | --- |
| C) fluoride dose | D) security and operational weaknesses |

Question 44. Backflow risk is highest where:

| A) tanks are full | B) a cross-connection exists with pressure reversal potential |
| --- | --- |
| C) no plumbing exists | D) only clean water exists |

Question 45. An air gap protects by:

| A) physical separation between potable and nonpotable sources | B) pH buffering |
| --- | --- |
| C) UV light | D) chemical reaction |

Question 46. Lead and copper compliance sampling focuses on:

| A) customer taps/premise plumbing under specified conditions | B) hydrants only |
| --- | --- |
| C) filter backwash only | D) raw water only |

Question 47. Corrosion control changes can affect:

| A) only pump horsepower | B) only source yield |
| --- | --- |
| C) lead/copper release and distribution stability | D) only tank level |

Question 48. If a process change improves turbidity but increases DBP formation potential, best response?

| A) stop monitoring | B) optimize the full treatment train rather than one metric alone |
| --- | --- |
| C) keep change forever | D) ignore DBPs |

Question 49. T5-level leadership means:

| A) only doing single calculations | B) avoiding communication |
| --- | --- |
| C) waiting for others only | D) anticipating system-wide consequences and directing safe, compliant response |

Question 50. In a serious treatment upset, the final priority should be:

| A) production convenience | B) public health and compliance |
| --- | --- |
| C) avoiding paperwork | D) keeping alarms quiet |

# Answer Key - T5 Practice Exam 06 - Advanced Scenario Mix

Batch ID: T5-20260619-E08-B6332

| Q | Answer | Review |
| --- | --- | --- |
| 1 | A | source-supported with caveats |
| 2 | C | source-supported with caveats |
| 3 | A | source-supported with caveats |
| 4 | C | source-supported with caveats |
| 5 | D | source-supported with caveats |
| 6 | A | source-supported with caveats |
| 7 | A | source-supported with caveats |
| 8 | B | source-supported with caveats |
| 9 | C | source-supported with caveats |
| 10 | C | source-supported with caveats |
| 11 | D | source-supported with caveats |
| 12 | A | source-supported with caveats |
| 13 | A | source-supported with caveats |
| 14 | D | source-supported with caveats |
| 15 | D | source-supported with caveats |
| 16 | C | source-supported with caveats |
| 17 | C | source-supported with caveats |
| 18 | D | source-supported with caveats |
| 19 | D | source-supported with caveats |
| 20 | C | source-supported with caveats |
| 21 | A | source-supported with caveats |
| 22 | B | source-supported with caveats |
| 23 | A | source-supported with caveats |
| 24 | A | source-supported with caveats |
| 25 | A | source-supported with caveats |
| 26 | A | source-supported with caveats |
| 27 | B | source-supported with caveats |
| 28 | B | source-supported with caveats |
| 29 | C | source-supported with caveats |
| 30 | D | source-supported with caveats |
| 31 | B | source-supported with caveats |
| 32 | B | source-supported with caveats |
| 33 | D | source-supported with caveats |
| 34 | D | source-supported with caveats |
| 35 | D | source-supported with caveats |
| 36 | D | source-supported with caveats |
| 37 | B | source-supported with caveats |
| 38 | C | source-supported with caveats |
| 39 | D | source-supported with caveats |
| 40 | C | source-supported with caveats |
| 41 | D | source-supported with caveats |
| 42 | B | source-supported with caveats |
| 43 | D | source-supported with caveats |
| 44 | B | source-supported with caveats |
| 45 | A | source-supported with caveats |
| 46 | A | source-supported with caveats |
| 47 | C | source-supported with caveats |
| 48 | B | source-supported with caveats |
| 49 | D | source-supported with caveats |
| 50 | B | source-supported with caveats |

# T5 Lab Procedures and Methods Mini Exam

Batch ID: T5-20260619-E09-B8699

Question 1. For drinking-water compliance monitoring, which source has the highest authority?

| A) Manufacturer catalog | B) Informal training handout |
| --- | --- |
| C) Current CFR and incorporated approved method text | D) Operator study note |

Question 2. Under routine RTCR total coliform/E. coli monitoring, the standard sample volume is usually:

| A) 100 mL | B) 10 L |
| --- | --- |
| C) 1 mL | D) 500 mL |

Question 3. For RTCR routine samples, presence/absence testing is generally:

| A) Only used for turbidity | B) Never allowed |
| --- | --- |
| C) Sufficient for total coliform/E. coli compliance | D) Used only for metals |

Question 4. Why is sodium thiosulfate used in microbiology sample bottles for chlorinated water?

| A) To add nutrients for algae | B) To preserve metals |
| --- | --- |
| C) To neutralize chlorine residual | D) To increase pH to 14 |

Question 5. A collection-to-incubation time beyond the approved holding window can:

| A) Improve sample reliability | B) Remove the need for documentation |
| --- | --- |
| C) Convert CFU to MPN automatically | D) Make a microbiological result questionable or invalid |

Question 6. CFU stands for:

| A) Carbon filtration units | B) Chlorine formation units |
| --- | --- |
| C) Certified fluoride uptake | D) Colony-forming units |

Question 7. MPN stands for:

| A) Minimum particle number | B) Meter probe normalization |
| --- | --- |
| C) Most probable number | D) Maximum pressure neutralization |

Question 8. HPC is best described as:

| A) A chlorine dose calculation | B) A metal digestion method |
| --- | --- |
| C) A general heterotrophic bacterial growth indicator | D) The same thing as an E. coli MCL |

Question 9. Which is an HPC method family captured in the lab section?

| A) Pour plate / plate count | B) Ion exchange softening |
| --- | --- |
| C) Lime-soda coagulation | D) Fluoride MCL averaging |

Question 10. Precision describes:

| A) The sample bottle size | B) Closeness to the true value only |
| --- | --- |
| C) Reproducibility of repeated results | D) The age of the instrument |

Question 11. Accuracy describes:

| A) How many samples are shipped | B) The color of a reagent |
| --- | --- |
| C) Closeness to the true or accepted value | D) Whether a sample is groundwater |

Question 12. Can results be precise but inaccurate?

| A) Only for turbidity | B) No |
| --- | --- |
| C) Only if pH is 7 | D) Yes |

Question 13. A blank is used mainly to check:

| A) Contamination or background contribution | B) Distribution pressure |
| --- | --- |
| C) Pump efficiency | D) Filter loading rate |

Question 14. A duplicate or replicate analysis is used mainly to check:

| A) Lead service line inventory | B) CT table compliance |
| --- | --- |
| C) Tank overflow elevation | D) Precision/repeatability |

Question 15. A spike or known addition is used mainly to check:

| A) Floc blanket depth | B) Pipe age |
| --- | --- |
| C) Accuracy/recovery | D) Valve direction |

Question 16. Chain of custody is important because it:

| A) Raises chlorine residual | B) Preserves sample traceability |
| --- | --- |
| C) Lowers turbidity | D) Replaces calibration |

Question 17. An analytical standard is used to:

| A) Clean the sink drain | B) Store waste acid |
| --- | --- |
| C) Calibrate or check a method | D) Increase sample hold time |

Question 18. Reagents should generally not be used past expiration because:

| A) Strength or purity may change | B) They become official regulations |
| --- | --- |
| C) They always become harmless | D) They stop needing labels |

Question 19. Reagent water quality matters because:

| A) It replaces QA/QC | B) It only affects taste panels |
| --- | --- |
| C) It can add background or interfere with analyses | D) It is used only for fire protection |

Question 20. The difference between concentration and acid/base strength is that:

| A) They are identical terms | B) Strength means bottle size |
| --- | --- |
| C) Concentration means sample temperature only | D) Concentration is amount present; strength is degree of ionization |

Question 21. Acids and bases should be stored separately because:

| A) They become more accurate together | B) They can react and release heat |
| --- | --- |
| C) They cancel documentation requirements | D) They are both sample preservatives only |

Question 22. Oxidizers and reducers should be stored separately because:

| A) They form perfect blanks | B) They lower sample temperature |
| --- | --- |
| C) They replace fume hoods | D) They can react vigorously |

Question 23. Beaker graduations are generally:

| A) Always NIST-certified | B) Used as legal standards |
| --- | --- |
| C) Approximate | D) More accurate than Class A pipets |

Question 24. A buret is commonly used to:

| A) Deliver measured titrant in titration | B) Store chlorine gas |
| --- | --- |
| C) Incubate microbiology samples | D) Measure pipe flow directly |

Question 25. A meniscus reading error affects:

| A) Filter media size only | B) Volume measurement |
| --- | --- |
| C) Pump horsepower only | D) Operator certification only |

Question 26. Analytical balances should be protected from drafts and vibration because:

| A) Vibration improves accuracy | B) These can affect mass readings |
| --- | --- |
| C) Drafts sterilize samples | D) Balances are only decorative |

Question 27. A titration endpoint is:

| A) The last sample of the month | B) The highest tank level |
| --- | --- |
| C) The method-defined point where the reaction is considered complete | D) The instrument serial number |

Question 28. A colorimetric test generally estimates concentration by:

| A) Pipe diameter | B) Color intensity from a chemical reaction |
| --- | --- |
| C) Pump speed | D) Valve torque |

Question 29. A turbidimetric method is based on:

| A) Valve position | B) Total organic carbon only |
| --- | --- |
| C) Cloudiness or light scatter | D) Taste threshold |

Question 30. pH and ion-selective electrodes require:

| A) Proper calibration and stable readings | B) Chlorine gas feed |
| --- | --- |
| C) No standards ever | D) Hot lime softening |

Question 31. Hardness is commonly associated with which method family in operator training?

| A) Cryptosporidium microscopy only | B) UV disinfection only |
| --- | --- |
| C) EDTA titration | D) Ozone CT only |

Question 32. Alkalinity is commonly associated with:

| A) Backflow device testing only | B) Titration-based methods |
| --- | --- |
| C) Virus enumeration only | D) Distribution flushing only |

Question 33. Residual chlorine testing may use:

| A) Only a balance | B) DPD colorimetric methods or amperometric titration, depending on approved context |
| --- | --- |
| C) Only a microscope | D) Only a jar test paddle |

Question 34. Turbidity is commonly measured by:

| A) Nephelometric methods | B) Colony counts |
| --- | --- |
| C) EDTA hardness titration | D) Sodium thiosulfate blanks only |

Question 35. Dissolved oxygen in older wet-chemistry training is associated with:

| A) Winkler method concepts | B) Fluoride secondary standard only |
| --- | --- |
| C) PFAS hazard index only | D) Lead and copper tap sampling only |

Question 36. Nitrate/nitrite and phosphate are often associated with:

| A) Colorimetric nutrient method families | B) Backwash rate only |
| --- | --- |
| C) Pressure-zone maps only | D) Valve exercising |

Question 37. A certified laboratory SOP should be treated as:

| A) Required operating direction for that lab/method | B) Less important than a quiz card |
| --- | --- |
| C) Optional decoration | D) A substitute for sample labeling |

Question 38. If an unusual lab result is received, the operator should first:

| A) Dispose of all records | B) Change the result to expected value |
| --- | --- |
| C) Verify sample identity/result status and follow SOP/supervisor/regulatory path | D) Ignore it until next month |

Question 39. Why should lab method versions matter?

| A) Versions only affect font size | B) Versions replace QA/QC |
| --- | --- |
| C) Versions never matter | D) Approval can depend on exact method version/date |

Question 40. What should be done before using a training-reference method as a compliance method?

| A) Assume it is approved forever | B) Crosscheck against CFR/EPA/state approved methods |
| --- | --- |
| C) Remove the method number | D) Skip certification requirements |

Question 41. The WEF lab techniques reference is best used as:

| A) The controlling drinking-water legal authority | B) A training/reference source for lab fundamentals |
| --- | --- |
| C) A substitute for SDS | D) A replacement for 40 CFR Part 141 |

Question 42. The Water and Wastewater Examination Manual is useful mainly for:

| A) Method-family awareness and QA/QC training | B) Replacing Standard Methods entirely |
| --- | --- |
| C) Setting PFAS MCLs | D) Current California legal text |

Question 43. The uploaded Water Quality Concepts files should be used carefully because:

| A) File-integrity issues were observed | B) They contain no sampling topics |
| --- | --- |
| C) They replace all EPA methods | D) They are official California Title 22 text |

Question 44. Which item belongs in lab QA/QC records?

| A) Calibration/check results | B) Pump paint color |
| --- | --- |
| C) Operator lunch schedule only | D) Tree trimming schedule |

Question 45. What is a common reason for using certified standards or certificates of analysis?

| A) To avoid calibration | B) To eliminate hold times |
| --- | --- |
| C) To prove a sample was not collected | D) Traceability and known quality |

Question 46. What is a key reason not to copy full method procedures into the vault?

| A) Method names are unimportant | B) Operators cannot learn concepts |
| --- | --- |
| C) Copyright/SOP concerns and need to keep study notes at operator-summary level | D) Flashcards require legal text only |

Question 47. Which source layer is strongest for drinking-water compliance method approval?

| A) Unverified quiz site | B) Social media summary |
| --- | --- |
| C) CFR / incorporated approved method | D) A handwritten shortcut with no source |

Question 48. What does “method recognition” mean in this vault?

| A) Memorizing every procedural step verbatim | B) Ignoring approved-method versions |
| --- | --- |
| C) Knowing what a method family is used for and its limits without replacing SOPs | D) Using any kit for any analyte |

Question 49. Why should water and wastewater method cards be tagged carefully?

| A) Drinking-water samples never need labs | B) Some methods/authorities differ between drinking-water compliance and wastewater permit testing |
| --- | --- |
| C) Wastewater methods automatically set drinking-water MCLs | D) Tags are only decorative |

Question 50. Before public release, lab-method cards should be:

| A) Published without review | B) Crosschecked against EPA/CFR/state sources and caveated where needed |
| --- | --- |
| C) Stripped of source IDs | D) Mixed with unsourced exam dumps |

# Answer Key - T5 Lab Procedures and Methods Mini Exam

Batch ID: T5-20260619-E09-B8699

| Q | Answer | Review |
| --- | --- | --- |
| 1 | C | source-supported with caveats |
| 2 | A | source-supported with caveats |
| 3 | C | source-supported with caveats |
| 4 | C | source-supported with caveats |
| 5 | D | source-supported with caveats |
| 6 | D | source-supported with caveats |
| 7 | C | source-supported with caveats |
| 8 | C | source-supported with caveats |
| 9 | A | source-supported with caveats |
| 10 | C | source-supported with caveats |
| 11 | C | source-supported with caveats |
| 12 | D | source-supported with caveats |
| 13 | A | source-supported with caveats |
| 14 | D | source-supported with caveats |
| 15 | C | source-supported with caveats |
| 16 | B | source-supported with caveats |
| 17 | C | source-supported with caveats |
| 18 | A | source-supported with caveats |
| 19 | C | source-supported with caveats |
| 20 | D | source-supported with caveats |
| 21 | B | source-supported with caveats |
| 22 | D | source-supported with caveats |
| 23 | C | source-supported with caveats |
| 24 | A | source-supported with caveats |
| 25 | B | source-supported with caveats |
| 26 | B | source-supported with caveats |
| 27 | C | source-supported with caveats |
| 28 | B | source-supported with caveats |
| 29 | C | source-supported with caveats |
| 30 | A | source-supported with caveats |
| 31 | C | source-supported with caveats |
| 32 | B | source-supported with caveats |
| 33 | B | source-supported with caveats |
| 34 | A | source-supported with caveats |
| 35 | A | source-supported with caveats |
| 36 | A | source-supported with caveats |
| 37 | A | source-supported with caveats |
| 38 | C | source-supported with caveats |
| 39 | D | source-supported with caveats |
| 40 | B | source-supported with caveats |
| 41 | B | source-supported with caveats |
| 42 | A | source-supported with caveats |
| 43 | A | source-supported with caveats |
| 44 | A | source-supported with caveats |
| 45 | D | source-supported with caveats |
| 46 | C | source-supported with caveats |
| 47 | C | source-supported with caveats |
| 48 | C | source-supported with caveats |
| 49 | B | source-supported with caveats |
| 50 | B | source-supported with caveats |

# T5 Cross Connection Control Mini Exam

Batch ID: T5-20260619-E10-B4494

Question 1. What is a cross-connection?

| A) A filter-to-waste valve | B) A chlorine sample point only |
| --- | --- |
| C) A finished-water storage tank | D) A physical or potential connection between potable water and a source of unknown or lesser quality |

Question 2. What is backflow?

| A) Filtered water entering a clearwell | B) Normal finished-water flow |
| --- | --- |
| C) Unwanted reverse flow into the potable water system | D) Routine hydrant flushing |

Question 3. Backsiphonage is caused by:

| A) Higher downstream pressure | B) Reduced supply pressure |
| --- | --- |
| C) High fluoride residual | D) Low hardness |

Question 4. Backpressure is caused by:

| A) Downstream pressure greater than supply pressure | B) Reduced supply pressure only |
| --- | --- |
| C) A sample tap | D) Low turbidity |

Question 5. Which method provides the strongest physical separation?

| A) Plain hose bibb | B) Unlisted adapter |
| --- | --- |
| C) Air gap | D) Single check valve |

Question 6. What does RP stand for?

| A) Reduced-pressure principle assembly | B) Residual pressure pipe |
| --- | --- |
| C) Reverse pump | D) Routine pressure |

Question 7. What does DC stand for in this context?

| A) Direct current | B) Distribution chlorine |
| --- | --- |
| C) Daily calculation | D) Double check valve assembly |

Question 8. A PVB protects against:

| A) Radionuclides only | B) Backpressure only |
| --- | --- |
| C) Backsiphonage only | D) Pump cavitation |

Question 9. An AVB is generally not used under:

| A) Continuous pressure | B) Point-of-use conditions |
| --- | --- |
| C) Open discharge conditions | D) Atmospheric conditions |

Question 10. A dual check is:

| A) A turbidity meter part | B) Always the same as an RP assembly |
| --- | --- |
| C) Not the same as a testable DC assembly | D) The highest physical separation |

Question 11. What is containment protection?

| A) Protection only inside a single faucet | B) A jar test method |
| --- | --- |
| C) Protection at the service connection | D) A chlorine demand test |

Question 12. What is isolation protection?

| A) Only a billing meter | B) Only protection at the water source |
| --- | --- |
| C) Only a tank screen | D) Protection at or near the internal hazard |

Question 13. AWWA C510 covers:

| A) All California rules | B) Double check valve backflow prevention assemblies |
| --- | --- |
| C) All field-test procedures | D) All wastewater lab methods |

Question 14. A complete DC assembly under AWWA C510 includes:

| A) Only a vacuum breaker | B) Only an air gap |
| --- | --- |
| C) One check valve and no test cocks | D) Two independent check valves, two shutoff valves, and four test cocks |

Question 15. AWWA C510 is best used for:

| A) Replacing tester procedures | B) Replacing local rules |
| --- | --- |
| C) DC assembly construction/design study points | D) Setting PFAS MCLs |

Question 16. Why must a testable assembly be accessible?

| A) It must be tested, maintained, repaired, or replaced | B) It must be hidden |
| --- | --- |
| C) It must be painted | D) It must always be buried |

Question 17. Why does RP drainage matter?

| A) RP assemblies never discharge | B) Drainage replaces testing |
| --- | --- |
| C) The relief valve may discharge and needs a safe location | D) Drainage proves pH compliance |

Question 18. What can an unprotected bypass do?

| A) Eliminate records | B) Defeat the intended protection |
| --- | --- |
| C) Replace the assembly | D) Improve testing automatically |

Question 19. Who controls actual approved installation and testing requirements?

| A) Authority having jurisdiction and program rules | B) Product catalog only |
| --- | --- |
| C) A random online quiz | D) Handwritten shortcut only |

Question 20. Which type protects against backsiphonage only and not backpressure?

| A) RP | B) Air gap |
| --- | --- |
| C) DC | D) PVB |

Question 21. Which type is commonly associated with high-hazard protection where approved?

| A) Pipe coupling | B) Hose adapter only |
| --- | --- |
| C) Single check valve | D) RP assembly |

Question 22. Which type is commonly limited to lower-hazard use where approved?

| A) Single check only | B) Unprotected bypass |
| --- | --- |
| C) Missing air gap | D) DC assembly |

Question 23. What should be recorded for an assembly program?

| A) Customer name only | B) Paint color only |
| --- | --- |
| C) Weather only | D) Type, size, model, serial number, location, test date, result, and tester information |

Question 24. What does a flow arrow show?

| A) Meter reading date | B) Required direction of flow |
| --- | --- |
| C) Pipe age | D) Pump horsepower |

Question 25. Which source is still needed for detailed field-test procedures?

| A) Taste chart | B) PFAS brochure |
| --- | --- |
| C) USC Foundation Manual or accepted local tester reference | D) Fluoride MCL table |

Question 26. Why is hazard level important?

| A) It replaces testing | B) It only determines pipe color |
| --- | --- |
| C) It determines the level of protection needed | D) It removes local authority requirements |

Question 27. Which is true about AWWA C510?

| A) It is the USC field-test manual | B) It is Title 22 |
| --- | --- |
| C) It is a standard for DC assemblies, not a complete program manual | D) It is a PFAS rule |

Question 28. Which item is usually part of a testable assembly?

| A) Fluoride probe only | B) Test cocks |
| --- | --- |
| C) Jar-test paddle | D) Sample incubator |

Question 29. What should happen when local rules are more specific than a study note?

| A) Ignore them | B) Follow the local rules |
| --- | --- |
| C) Use oldest note only | D) Use shortest answer |

Question 30. What is the best study caveat?

| A) They eliminate testing requirements | B) Study aids do not replace approved program rules or tester procedures |
| --- | --- |
| C) They replace all manuals | D) They are official exam questions |

# Answer Key - T5 Cross Connection Control Mini Exam

Batch ID: T5-20260619-E10-B4494

| Q | Answer | Review |
| --- | --- | --- |
| 1 | D | source-supported with caveats |
| 2 | C | source-supported with caveats |
| 3 | B | source-supported with caveats |
| 4 | A | source-supported with caveats |
| 5 | C | source-supported with caveats |
| 6 | A | source-supported with caveats |
| 7 | D | source-supported with caveats |
| 8 | C | source-supported with caveats |
| 9 | A | source-supported with caveats |
| 10 | C | source-supported with caveats |
| 11 | C | source-supported with caveats |
| 12 | D | source-supported with caveats |
| 13 | B | source-supported with caveats |
| 14 | D | source-supported with caveats |
| 15 | C | source-supported with caveats |
| 16 | A | source-supported with caveats |
| 17 | C | source-supported with caveats |
| 18 | B | source-supported with caveats |
| 19 | A | source-supported with caveats |
| 20 | D | source-supported with caveats |
| 21 | D | source-supported with caveats |
| 22 | D | source-supported with caveats |
| 23 | D | source-supported with caveats |
| 24 | B | source-supported with caveats |
| 25 | C | source-supported with caveats |
| 26 | C | source-supported with caveats |
| 27 | C | source-supported with caveats |
| 28 | B | source-supported with caveats |
| 29 | B | source-supported with caveats |
| 30 | B | source-supported with caveats |

# T5 Distribution Source Hydrants and Disinfection Mini Exam

Batch ID: T5-20260619-E11-B7088

Question 1. What is the main purpose of a drinking water distribution system?

| A) Replace all treatment | B) Eliminate all sampling |
| --- | --- |
| C) Store untreated wastewater | D) Deliver potable water to customers while maintaining pressure, flow, and water quality |

Question 2. Which list best represents distribution-system components?

| A) Only lab incubators | B) Mains, valves, hydrants, storage, pumps, meters, and services |
| --- | --- |
| C) Only jar-test paddles | D) Only source-water intakes |

Question 3. Why are looped distribution systems generally preferred over dead ends?

| A) They prevent all pipe breaks | B) They remove the need for valves |
| --- | --- |
| C) They improve circulation, redundancy, and operational flexibility | D) They eliminate disinfection |

Question 4. What water-quality issue is common in dead ends or low-flow areas?

| A) Elimination of sediment | B) No need for flushing |
| --- | --- |
| C) Increased membrane salt rejection | D) Increased water age and residual loss |

Question 5. What does AWWA G200 primarily support in this vault?

| A) Rainfall maps only | B) Lab incubation only |
| --- | --- |
| C) Distribution-system operation and management concepts | D) PFAS federal MCL values |

Question 6. What is a key caveat for AWWA standards?

| A) They replace all state rules | B) They are quiz sites |
| --- | --- |
| C) They are not complete specifications and do not supersede law or code | D) They prohibit local requirements |

Question 7. What are transmission lines?

| A) Larger pipelines that move water between major system components | B) Chlorine tablets only |
| --- | --- |
| C) Turbidity standards only | D) Lab glassware |

Question 8. Why does pipe material selection matter?

| A) It affects pressure capacity, corrosion, installation, water quality, and service life | B) It only affects color |
| --- | --- |
| C) It eliminates maintenance | D) It replaces hydraulic design |

Question 9. What does pipe C value relate to?

| A) Coliform results only | B) Chloramine breakpoint only |
| --- | --- |
| C) Calcium hardness only | D) Hydraulic roughness/friction in flow calculations |

Question 10. What is one purpose of distribution storage?

| A) Replace all pumps | B) Store sewage |
| --- | --- |
| C) Balance demand and support pressure/emergency supply | D) Eliminate residual monitoring |

Question 11. Why are valves important in distribution?

| A) They replace all hydrants | B) Isolation, control, flushing, maintenance, and emergency response |
| --- | --- |
| C) They eliminate all water age | D) They are only used in labs |

Question 12. What is the primary purpose of a fire hydrant?

| A) Fluoride analysis | B) Incubation |
| --- | --- |
| C) Public fire protection service | D) Chemical coagulation |

Question 13. Which hydrant type is intended for freezing climates?

| A) Lab hydrant | B) Wet-only hydrant |
| --- | --- |
| C) Membrane hydrant | D) Dry-barrel fire hydrant |

Question 14. Which AWWA standard covers dry-barrel fire hydrants?

| A) ANSI/AWWA C510 | B) ANSI/AWWA C502 |
| --- | --- |
| C) ANSI/AWWA B112 | D) ANSI/AWWA B600 |

Question 15. Why should non-fire hydrant use be restricted and controlled?

| A) To avoid valves | B) To maintain hydrants for fire emergencies and protect water quality |
| --- | --- |
| C) To remove chlorine | D) To eliminate records |

Question 16. If a hydrant cannot be opened or closed by one person using a proper hydrant wrench, what is the best response?

| A) Remove all hydrants | B) Repair it instead of forcing it |
| --- | --- |
| C) Ignore it | D) Force it |

Question 17. Why can using a hydrant to dispense drinking water require special care?

| A) Water never contacts surfaces | B) Downstream surfaces may need disinfection and material-suitability evaluation |
| --- | --- |
| C) Hydrants sterilize automatically | D) Hydrants eliminate risk |

Question 18. What AWWA manual is commonly paired with hydrant maintenance topics?

| A) AWWA M17 | B) AWWA B403 |
| --- | --- |
| C) AWWA B600 | D) AWWA B114 |

Question 19. Why is distribution-system disinfection important?

| A) It removes treatment | B) Distribution deficiencies can contribute to contamination risk |
| --- | --- |
| C) It replaces pressure | D) It eliminates sampling |

Question 20. What is a common contamination source during water main installation or repair?

| A) Spreadsheet formatting | B) Soil, sediment, trench water, or foreign water entering pipe/appurtenances |
| --- | --- |
| C) UV serial number | D) CCR wording |

Question 21. Which sequence best fits pipeline disinfection work?

| A) Inspection, sanitary construction, flushing/cleaning, disinfection, final flushing, bacteriological testing, connection, documentation | B) Jar test only |
| --- | --- |
| C) Skip inspection | D) Paint pipe only |

Question 22. What are common storage-facility contamination routes?

| A) pH meters only | B) Clean sample bottles only |
| --- | --- |
| C) Sealed hatches only | D) Open/missing vents, hatches, roof openings, inspection activities, and foreign matter |

Question 23. Which AWWA standards are commonly tied to water main and storage disinfection?

| A) B112 and B114 only | B) C651 and C652 |
| --- | --- |
| C) B600 and B604 only | D) C502 and C510 only |

Question 24. Why is bacteriological testing part of disinfection work?

| A) It confirms paint color | B) It measures pipe C value |
| --- | --- |
| C) It helps verify sanitary conditions before return to potable service | D) It replaces disinfection |

Question 25. Why may dechlorination be needed after disinfection?

| A) Highly chlorinated water may need treatment before discharge | B) It replaces sampling |
| --- | --- |
| C) Chlorine disappears instantly | D) It increases pipe roughness |

Question 26. Which chemicals are commonly used for pipeline/storage disinfection?

| A) Only carbon | B) Liquid chlorine, sodium hypochlorite, and calcium hypochlorite |
| --- | --- |
| C) Only alum | D) Only table salt |

Question 27. Which free-chlorine species is more effective as a disinfectant?

| A) Hypochlorite ion | B) Nitrate |
| --- | --- |
| C) Hypochlorous acid | D) Calcium carbonate |

Question 28. What happens to chlorine effectiveness as pH rises?

| A) More free chlorine shifts toward less-effective hypochlorite ion | B) Chlorine becomes turbidity |
| --- | --- |
| C) Chlorine becomes more acidic | D) Chlorine becomes PFAS |

Question 29. What does AWWA M20 support?

| A) Only jar-test math | B) Only wells |
| --- | --- |
| C) Chlorination/chloramination practice, chemistry, equipment, safety, strategy, and residual testing | D) Only fire hose threads |

Question 30. What does AWWA B403 cover?

| A) Fire hydrants | B) Cross-connection assemblies |
| --- | --- |
| C) Aluminum sulfate | D) Membrane systems |

Question 31. What is aluminum sulfate commonly used for?

| A) Fire-flow testing only | B) Backflow testing only |
| --- | --- |
| C) Hydrant operation | D) Coagulation |

Question 32. What does AWWA B600 cover?

| A) RO/NF systems | B) Dry-barrel hydrants |
| --- | --- |
| C) Aluminum sulfate | D) Powdered activated carbon |

Question 33. What does AWWA B604 cover?

| A) PFAS timing only | B) Granular activated carbon |
| --- | --- |
| C) Program management only | D) Hydrant color only |

Question 34. What is activated carbon commonly used for?

| A) Raising all residuals | B) Replacing hydrants |
| --- | --- |
| C) Adsorbing taste-and-odor compounds and some organic contaminants | D) Measuring pipe wall thickness |

Question 35. What does AWWA B112 cover?

| A) Double-check assemblies | B) Microfiltration and ultrafiltration membrane systems |
| --- | --- |
| C) Dry-barrel hydrants | D) Aluminum sulfate |

Question 36. What does AWWA B114 cover?

| A) Hydrant color only | B) Water main disinfection only |
| --- | --- |
| C) Powdered carbon only | D) Reverse osmosis and nanofiltration systems |

Question 37. Which membrane group generally removes dissolved material better?

| A) MF/UF | B) Fire hydrants |
| --- | --- |
| C) RO/NF | D) Dead-end mains |

Question 38. Why is the uploaded Water Sources file caveated?

| A) It is blank | B) It has valid AWWA front matter but also suspicious non-book/unrelated parsed text |
| --- | --- |
| C) It is only a hydrant standard | D) It is official California regulation |

Question 39. Product standards should be paired with operator/training references because:

| A) Site conditions never matter | B) Product standards are never useful |
| --- | --- |
| C) Product standards do not fully explain operations, troubleshooting, or site-specific design | D) Operator references override all laws |

Question 40. What controls final installation, operation, and compliance decisions?

| A) Current regulations, state/local rules, authority having jurisdiction, engineering design, manufacturer instructions, and utility SOPs | B) A single old workbook only |
| --- | --- |
| C) Flashcards only | D) The shortest answer choice |

# Answer Key - T5 Distribution Source Hydrants and Disinfection Mini Exam

Batch ID: T5-20260619-E11-B7088

| Q | Answer | Review |
| --- | --- | --- |
| 1 | D | source-supported with caveats |
| 2 | B | source-supported with caveats |
| 3 | C | source-supported with caveats |
| 4 | D | source-supported with caveats |
| 5 | C | source-supported with caveats |
| 6 | C | source-supported with caveats |
| 7 | A | source-supported with caveats |
| 8 | A | source-supported with caveats |
| 9 | D | source-supported with caveats |
| 10 | C | source-supported with caveats |
| 11 | B | source-supported with caveats |
| 12 | C | source-supported with caveats |
| 13 | D | source-supported with caveats |
| 14 | B | source-supported with caveats |
| 15 | B | source-supported with caveats |
| 16 | B | source-supported with caveats |
| 17 | B | source-supported with caveats |
| 18 | A | source-supported with caveats |
| 19 | B | source-supported with caveats |
| 20 | B | source-supported with caveats |
| 21 | A | source-supported with caveats |
| 22 | D | source-supported with caveats |
| 23 | B | source-supported with caveats |
| 24 | C | source-supported with caveats |
| 25 | A | source-supported with caveats |
| 26 | B | source-supported with caveats |
| 27 | C | source-supported with caveats |
| 28 | A | source-supported with caveats |
| 29 | C | source-supported with caveats |
| 30 | C | source-supported with caveats |
| 31 | D | source-supported with caveats |
| 32 | D | source-supported with caveats |
| 33 | B | source-supported with caveats |
| 34 | C | source-supported with caveats |
| 35 | B | source-supported with caveats |
| 36 | D | source-supported with caveats |
| 37 | C | source-supported with caveats |
| 38 | B | source-supported with caveats |
| 39 | C | source-supported with caveats |
| 40 | A | source-supported with caveats |

# Supplemental Regulations, Source Water, and Situational Practice

Batch ID: T5-SUPPLEMENTAL-REG-SOURCE-BLENDING-20260621

Question 1. Which federal law authorizes EPA to set national health-based drinking water standards for public water systems?

| A) Clean Water Act | B) Safe Drinking Water Act |
| --- | --- |
| C) Porter-Cologne Water Quality Control Act | D) California Water Code |

Question 2. Which federal regulation part contains National Primary Drinking Water Regulations for public water systems?

| A) 40 CFR Part 141 | B) 40 CFR Part 142 |
| --- | --- |
| C) 40 CFR Part 143 | D) 29 CFR Part 1910 |

Question 3. Which federal regulation part is most associated with state primacy and implementation of the drinking-water program?

| A) 40 CFR Part 141 | B) 40 CFR Part 142 |
| --- | --- |
| C) 40 CFR Part 143 | D) CCR Title 17 |

Question 4. Which federal regulation part covers National Secondary Drinking Water Regulations?

| A) 40 CFR Part 141 | B) 40 CFR Part 142 |
| --- | --- |
| C) 40 CFR Part 143 | D) CCR Title 22 Chapter 13 |

Question 5. For California drinking-water MCLs and routine drinking-water monitoring requirements, which source should an operator expect to use most often?

| A) CCR Title 22 | B) Clean Water Act NPDES permit only |
| --- | --- |
| C) OSHA respiratory protection standard | D) Local plumbing code only |

Question 6. For current California cross-connection control program requirements, what should operators treat as the current controlling source?

| A) Old Title 17 articles only | B) Cross-Connection Control Policy Handbook |
| --- | --- |
| C) Consumer Confidence Report rule | D) Radionuclides Rule |

Question 7. California T1 through T5 and D1 through D5 operator certification requirements are primarily associated with which California regulation area?

| A) Title 22 operator certification rules | B) Stage 2 DBPR only |
| --- | --- |
| C) AWIA emergency response plan rules only | D) 40 CFR Part 143 only |

Question 8. Which rule family is most directly tied to routine bacteriological monitoring, total coliform, E. coli findings, assessments, and corrective action?

| A) Radionuclides Rule | B) Revised Total Coliform Rule |
| --- | --- |
| C) Lead and Copper Rule | D) Stage 2 DBPR |

Question 9. Which rule family is most associated with filtration, turbidity performance, CT, Giardia, viruses, and Cryptosporidium?

| A) Surface Water Treatment Rule family | B) Consumer Confidence Report Rule |
| --- | --- |
| C) Public Notification Rule | D) UCMR |

Question 10. Which rule family is most associated with TTHM and HAA5 compliance?

| A) Stage 1 and Stage 2 Disinfectants and Disinfection Byproducts Rules | B) Ground Water Rule |
| --- | --- |
| C) Radionuclides Rule | D) Lead and Copper Rule |

Question 11. Lead and copper compliance is most associated with which regulatory concept?

| A) Secondary MCL only | B) Action level and corrosion control framework |
| --- | --- |
| C) Radionuclide gross alpha only | D) Surface-water CT table only |

Question 12. A confirmed E. coli positive routine sample is reported. What is the best operator response?

| A) Wait for the annual CCR cycle before doing anything | B) Follow the bacteriological rule response plan, notify required contacts, and coordinate repeat/corrective action requirements |
| --- | --- |
| C) Only increase billing inserts | D) Ignore it if chlorine residual is usually present |

Question 13. A source-water blending calculation is usually based on which principle?

| A) The highest source concentration always becomes the blended concentration | B) Flow-weighted concentration from each source |
| --- | --- |
| C) The lowest source concentration always becomes the blended concentration | D) Only tank volume matters; source flow does not |

Question 14. Source A is 2 MGD at 8 mg/L nitrate and Source B is 1 MGD at 2 mg/L nitrate. Approximate blended nitrate is:

| A) 3.0 mg/L | B) 5.0 mg/L |
| --- | --- |
| C) 6.0 mg/L | D) 10.0 mg/L |

Question 15. A high-arsenic well is 0.5 MGD at 12 ug/L and a low-arsenic source is 1.5 MGD at 4 ug/L. Approximate blended arsenic is:

| A) 2 ug/L | B) 6 ug/L |
| --- | --- |
| C) 8 ug/L | D) 16 ug/L |

Question 16. Before changing source-water blending ratios for compliance, what should a chief operator do first?

| A) Change valves and wait for complaints | B) Verify permit/operational limits, calculate expected quality, coordinate required monitoring, and document the change |
| --- | --- |
| C) Assume blending always removes all contaminants | D) Stop all compliance sampling |

Question 17. A new source blend may lower nitrate but increase TDS and customer taste complaints. What is the best operator-level concern?

| A) Only the nitrate result matters | B) Both primary compliance and secondary/aesthetic water quality impacts should be evaluated |
| --- | --- |
| C) Taste complaints prove the water is unsafe | D) Secondary standards override all primary standards |

Question 18. A wildfire causes loss of power, pressure fluctuations, and possible source-water ash impacts. What is the best T5-level first move?

| A) Wait until all lab results are complete before communicating internally | B) Activate the emergency response plan, stabilize pressure/treatment, coordinate notifications, and begin required monitoring |
| --- | --- |
| C) Disable SCADA alarms | D) Assume finished water is unaffected |

Question 19. A monitoring result is above an MCL. Which action is most appropriate?

| A) Erase the sample from the log if a resample might pass | B) Follow the applicable confirmation, reporting, public-notice, and corrective-action requirements |
| --- | --- |
| C) Only tell customers if they ask | D) Wait until next year's CCR before reviewing the result |

Question 20. A customer asks why the system issued a Tier 1 public notice. What is the best general explanation?

| A) Tier 1 is for situations with immediate potential health concern requiring rapid public notice | B) Tier 1 is only an annual education notice |
| --- | --- |
| C) Tier 1 is only for billing errors | D) Tier 1 means no operational response is needed |

Question 21. A compliance sample was analyzed by a lab that is not properly accredited for the method. What is the best concern?

| A) The result may not be acceptable for compliance reporting | B) The result is automatically better than an accredited result |
| --- | --- |
| C) Accreditation matters only for wastewater | D) The operator can certify the lab result personally |

Question 22. Which law is more associated with wastewater discharges, NPDES permits, and source-water protection context than finished drinking-water MCLs?

| A) Clean Water Act | B) Lead and Copper Rule |
| --- | --- |
| C) Consumer Confidence Report Rule | D) Title 22 operator certification |

Question 23. Which California law is most associated with broad water-quality control, basin planning, and discharge/source-water context?

| A) Porter-Cologne Water Quality Control Act | B) 40 CFR Part 143 |
| --- | --- |
| C) AWIA Section 2013 only | D) Stage 2 DBPR |

Question 24. Which federal rule requires annual water quality reporting to consumers?

| A) Consumer Confidence Report Rule | B) Ground Water Rule |
| --- | --- |
| C) Radionuclides Rule | D) UCMR only |

Question 25. Which rule area is most associated with gross alpha, uranium, radium, and beta/photon emitters?

| A) Radionuclides Rule | B) Stage 2 DBPR |
| --- | --- |
| C) Ground Water Rule | D) Public Notification Rule |

Question 26. PFAS monitoring and MCL implementation is most associated with which area?

| A) The federal PFAS National Primary Drinking Water Regulation and state implementation requirements | B) Only the old Title 17 cross-connection articles |
| --- | --- |
| C) Only OSHA lockout/tagout | D) Only secondary aesthetic standards |

Question 27. A filter effluent turbidity trend rises after a source blend change. What should the operator check first?

| A) Only customer billing records | B) Raw water quality, coagulant dose/jar testing, filter performance, and monitoring requirements |
| --- | --- |
| C) Nothing; blending cannot affect treatment | D) Only the next annual CCR |

Question 28. A source blend lowers turbidity but increases chlorine demand. What should the operator evaluate?

| A) Whether disinfectant dose, contact time, residual, and DBP risk remain acceptable | B) Only the color of the pump station |
| --- | --- |
| C) Nothing, because lower turbidity always solves every issue | D) Only the billing meter |

Question 29. A chlorine feed pump loses prime during peak demand. What is the best operator response?

| A) Document it at the end of the month only | B) Restore/backup feed safely, verify residuals, assess affected water, notify supervision, and follow SOP/reporting triggers |
| --- | --- |
| C) Turn off all alarms | D) Assume contact time alone is always enough |

Question 30. A flow of 1,496 gpm is approximately:

| A) 1.50 MGD | B) 1.08 MGD |
| --- | --- |
| C) 3.0 MGD | D) 2.15 MGD |

# Answer Key - Supplemental Regulations, Source Water, and Situational Practice

Batch ID: T5-SUPPLEMENTAL-REG-SOURCE-BLENDING-20260621

| Q | Answer | Review |
| --- | --- | --- |
| 1 | B | The SDWA is the main federal drinking-water law authorizing EPA drinking-water standards for public water systems. |
| 2 | A | 40 CFR Part 141 contains the National Primary Drinking Water Regulations. |
| 3 | B | 40 CFR Part 142 addresses implementation, primacy, and related state program requirements. |
| 4 | C | 40 CFR Part 143 is the secondary drinking-water regulation part. |
| 5 | A | California drinking-water standards and monitoring are primarily in CCR Title 22. |
| 6 | B | California replaced prior Title 17 cross-connection regulations with the Cross-Connection Control Policy Handbook. |
| 7 | A | California operator certification requirements are in the Title 22 operator certification framework. |
| 8 | B | The Revised Total Coliform Rule covers the total coliform/E. coli bacteriological framework and assessment response. |
| 9 | A | Surface-water treatment rules address filtration, disinfection, turbidity, CT, and microbial inactivation/removal targets. |
| 10 | A | The DBPR rule family covers disinfectants and disinfection byproducts such as TTHM and HAA5. |
| 11 | B | Lead and copper compliance uses action levels and corrosion-control related requirements rather than a simple finished-water MCL model. |
| 12 | B | A confirmed E. coli issue requires rule-driven response, notification/coordination, and corrective action handling. |
| 13 | B | Blended water quality is estimated with a flow-weighted concentration from each contributing source. |
| 14 | C | ((2 x 8) + (1 x 2)) / 3 = 6 mg/L. |
| 15 | B | ((0.5 x 12) + (1.5 x 4)) / 2.0 = 6 ug/L. |
| 16 | B | Source blending changes can affect compliance and distribution quality, so they should be calculated, documented, and coordinated with required monitoring/permits. |
| 17 | B | Blending decisions should consider enforceable health standards and secondary/aesthetic impacts that affect distribution quality and customers. |
| 18 | B | Emergency response should stabilize operations, coordinate communication, and start appropriate monitoring and notifications. |
| 19 | B | MCL exceedances trigger rule-specific confirmation, reporting, public notification, and corrective-action requirements. |
| 20 | A | Tier 1 public notice is used for the most urgent drinking-water situations with immediate potential health concern. |
| 21 | A | Compliance samples generally need proper approved methods and accredited laboratory handling for regulatory acceptance. |
| 22 | A | The Clean Water Act is mainly tied to water pollution control and discharges, though it affects source-water context. |
| 23 | A | Porter-Cologne is California's broad water-quality control law, more source/discharge oriented than operator MCL tables. |
| 24 | A | The Consumer Confidence Report Rule is the annual customer water-quality report framework. |
| 25 | A | The radionuclides rule area covers gross alpha, uranium, radium, and beta/photon emitters. |
| 26 | A | PFAS requirements are part of the emerging/current drinking-water regulatory program and are implemented through federal and state compliance processes. |
| 27 | B | A source blend can change treatment demand, so raw water quality and process-control checks are appropriate. |
| 28 | A | Blending can shift disinfection demand and DBP formation potential, so dose, residual, contact time, and DBP risk should be reviewed. |
| 29 | B | A disinfectant feed failure requires safe restoration, verification of residual and affected water, and escalation under SOP/regulatory triggers. |
| 30 | D | 1,496 gpm x 1,440 min/day = 2,154,240 gal/day, or about 2.15 MGD. |